## csp-guru
Power_station | Local_spelling | OpenCSP_ID | Country | Region | Status | Capacity_MW | Expected_generation_CSP_GWh_per_yr | Expected_generation_hybrid_GWh_per_yr | Capacity_factor | Technology | Hybridisation_capacity | Hybridisation_ratio | Hybridisation_comment | Year_construction_start | Year_operational | State_highest_administrative_level | Province_County_medium_administrative_level | City_lowest_administrative_level | Location_coordinates | DNI_kWh_per_m2_per_yr | Total_cost_million_currency_non_deflated | Cost_currency | Currency_year | Total_cost_million_USD2020 | Specific_cost_USD2020_per_kW | LCOE_5_25_USD2020_per_kWh | Remuneration_currency_per_kWh | Support_currency | Cost_year_remuneration | Remuneration_USD2020_per_kWh_deflated | PPA_or_support_duration_yr | Support_scheme_type | Policy_support_scheme | Concessional_funding_other_support | Land_area_whole_station_not_solar_field_km2 | Developer | Developer_country | First_owner | First_operator | Electricity_generation_offtaker | EPC | EPC_country | HTF_manufacturer | HTF_manufacturer_country | HTF_medium_or_product | HTF_category | Steam_turbine_manufacturer | Steam_turbine_manufacturer_country | Turbine_model | Turbine_thermodynamic_cycle | Power_cycle_pressure_bar | Turbine_efficiency_percent | Heat_exchanger_manufacturer | Heat_exchanger_manufacturer_country | Cooling_type | Energy_storage_type | Storage_capacity_hours | Storage_description | TES_engineering_company | TES_engineering_company_country | Solar_receiver_manufacturer | Solar_receiver_country | Solar_receiver_model | Tower_height_m | Number_of_heat_collecting_elements_for_trough_and_fresnel | Receiver_inlet_temperature_Celsius | Receiver_outlet_temperature_Celsius | SCA_or_heliostat_manufacturer | SCA_or_heliostat_manufacturer_country | SCA_or_heliostat_engineering_or_IP_owner_company | SCA_or_heliostat_engineering_or_IP_owner_company_country | SCA_or_heliostat_model | Reflector_mirror_manufacturer | Reflector_mirror_manufacturer_country | Reflector_model | Solar_mirror_area_m2 | Solar_multiple | Number_of_heliostats_or_dishes | Mirror_area_per_heliostat_or_dish | Fresnel_line_width_m | Fresnel_number_of_lines | Fresnel_line_length_m | Trough_solar_collector_area_m2 | Trough_SCA_length_m | Trough_number_of_loops | Trough_number_of_modules_per_SCA | Trough_number_of_SCA | Trough_number_of_SCA_per_loop | Construction_jobs_years | Annual_operations_jobs | Additional_sources_relative_to_2019_version_of_cspGURU_and_NRELSolarPACES_as_of_31_January_2020
Solar Electric Generating Station I |  | 1 | United States | North America | Decommissioned | 13.8 | 16.5 |  | 13.65% | Parabolic Trough |  |  | Natural gas boiler |  | 1984 | California |  | Daggett | 34.863,-116.827 | 2885 | 62.1 | USD | 2017 | 129.34 | 9372.4 | 0.67 | [5 empty] | PPA | PURPA Qualifying Facility Independent Power Producer, with special Standard Offer 2 (SO-2) type power purchase agreement to Southern California Edison | PURPA; Accelerated depreciation; Federal and state investment incentives; Solar property tax exclusion |  | Luz | USA | Cogentrix | Cogentrix | Southern California Edison |  |  |  |  | Calloria mineral oil | Thermal oil/organics |  |  |  |  | 40 | 31.5 |  |  | Wet | 2-tank direct | 3 | Storage system was damaged by fire in 1999 and was not replaced |  |  | Solel | Israel |  |  |  |  | 307 |  |  | Luz | USA | LS-1 | Flabeg | Germany | RP1 | 82960 | 1.0019
Solar Electric Generating Station II |  | 2 | United States | North America | Decommissioned | 30 | 32.5 |  | 12.37% | Parabolic Trough |  |  | Natural gas boiler |  | 1985 | California |  | Daggett | 34.863,-116.827 | 2885 | 135 | USD | 2017 | 272.46 | 9082 | 0.72 | [5 empty] | PPA | PURPA Qualifying Facility Independent Power Producer, with special Standard Offer 2 (SO-2) type power purchase agreement to Southern California Edison | PURPA; Accelerated depreciation; Federal and state investment incentives; Solar property tax exclusion |  | Luz | USA | Cogentrix | Cogentrix | Southern California Edison |  |  | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics |  |  |  |  | 40 | 29.4 |  |  | Wet | [5 empty] | Solel | Israel | UVAC |  |  |  | 316 |  |  | Luz | USA | LS-1 | Flabeg | Germany | RP2 | 190338 | 1.0574
Solar Electric Generating Station III |  | 3 | United States | North America | Decommissioned | 30 | 68.55 |  | 26.08% | Parabolic Trough |  |  | Natural gas boiler |  | 1985 | California |  | Kramer Junction | 35.014,-117.559 | 2987 | 102 | USD | 1985 | 205.86 | 6861.9 | 0.26 | [5 empty] | PPA | PURPA Qualifying Facility Independent Power Producer, with special Standard Offer 2 (SO-2) type power purchase agreement to Southern California Edison | PURPA; Accelerated depreciation; Federal and state investment incentives; Solar property tax exclusion |  | Luz | USA | NextEra | NextEra | Southern California Edison |  |  | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics |  |  |  |  | 40 | 30.6 |  |  | Wet | [5 empty] | Solel | Israel | UVAC |  |  |  | 349 |  |  | Luz | USA | LS-2 | Flabeg | Germany | RP2 | 230300 | 1.2794 | [13 empty] | https://web.archive.org/web/20210921090026/https://www.eia.gov/todayinenergy/detail.php?id=49616
Solar Electric Generating Station IV |  | 4 | United States | North America | Decommissioned | 30 | 68.28 |  | 25.98% | Parabolic Trough |  |  | Natural gas boiler |  | 1989 | California |  | Kramer Junction | 35.014,-117.559 | 2987 | 102 | USD | 1989 | 183 | 6099.9 | 0.23 | [5 empty] | PPA | PURPA Qualifying Facility Independent Power Producer, with special Standard Offer 2 (SO-2) type power purchase agreement to Southern California Edison | PURPA; Accelerated depreciation; Federal and state investment incentives; Solar property tax exclusion |  | Luz | USA | NextEra | NextEra | Southern California Edison |  |  | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics |  |  |  |  | 40 | 30.6 |  |  | Wet | [5 empty] | Solel | Israel | UVAC |  |  |  | 349 |  |  | Luz | USA | LS-2 | Flabeg | Germany | RP2 | 230300 | 1.2794 | [13 empty] | https://web.archive.org/web/20210921090026/https://www.eia.gov/todayinenergy/detail.php?id=49616
Solar Electric Generating Station V |  | 5 | United States | North America | Decommissioned | 30 | 72.88 |  | 27.73% | Parabolic Trough |  |  | Natural gas boiler |  | 1989 | California |  | Kramer Junction | 35.014,-117.559 | 2987 | 102 | USD | 1989 | 183 | 6099.9 | 0.22 | [5 empty] | PPA | PURPA Qualifying Facility Independent Power Producer, with special Standard Offer 2 (SO-2) type power purchase agreement to Southern California Edison | PURPA; Accelerated depreciation; Federal and state investment incentives; Solar property tax exclusion |  | Luz | USA | NextEra | NextEra | Southern California Edison |  |  | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics |  |  |  |  | 40 | 30.6 |  |  | Wet | [5 empty] | Solel | Israel | UVAC |  |  |  | 349 |  |  | Luz | USA | LS-2 | Flabeg | Germany | RP3 | 250500 | 1.3917 | [13 empty] | https://web.archive.org/web/20210921090026/https://www.eia.gov/todayinenergy/detail.php?id=49616
Solar Electric Generating Station VI |  | 6 | United States | North America | Decommissioned | 30 | 67.76 |  | 25.78% | Parabolic Trough |  |  | Natural gas boiler |  | 1989 | California |  | Kramer Junction | 35.014,-117.559 | 2987 | 102 | USD | 1989 | 183 | 6099.9 | 0.23 | [5 empty] | PPA | PURPA Qualifying Facility Independent Power Producer, with special Standard Offer 2 (SO-2) type power purchase agreement to Southern California Edison | PURPA; Accelerated depreciation; Federal and state investment incentives; Solar property tax exclusion |  | Luz | USA | NextEra | NextEra | Southern California Edison |  |  | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics |  |  |  |  | 100 | 37.5 |  |  | Wet | [5 empty] | Solel | Israel | UVAC |  |  |  | 390 |  |  | Luz | USA | LS-2 | Flabeg | Germany | RP3 | 188000 | 1.0444 | [13 empty] | https://web.archive.org/web/20210921090026/https://www.eia.gov/todayinenergy/detail.php?id=49616
Solar Electric Generating Station VII |  | 7 | United States | North America | Decommissioned | 30 | 65.05 |  | 24.75% | Parabolic Trough |  |  | Natural gas boiler |  | 1989 | California |  | Kramer Junction | 35.014,-117.559 | 2987 | 102 | USD | 1989 | 183 | 6099.9 | 0.24 | [5 empty] | PPA | PURPA Qualifying Facility Independent Power Producer, with special Standard Offer 2 (SO-2) type power purchase agreement to Southern California Edison | PURPA; Accelerated depreciation; Federal and state investment incentives; Solar property tax exclusion |  | Luz | USA | NextEra | NextEra | Southern California Edison |  |  | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics |  |  |  |  | 100 | 37.5 |  |  | Wet | [5 empty] | Solel | Israel | UVAC |  |  |  | 390 |  |  | Luz | USA | LS-2 | Flabeg | Germany | RP3 | 194280 | 1.0793 | [13 empty] | https://web.archive.org/web/20210921090026/https://www.eia.gov/todayinenergy/detail.php?id=49616
Solar Electric Generating Station VIII |  | 8 | United States | North America | Decommissioned | 80 | 137.99 |  | 19.69% | Parabolic Trough |  |  | Natural gas boiler |  | 1989 | California |  | Harper Dry Lake | 35.032,-117.348 | 2893 | 230 | USD | 1989 | 412.64 | 5158 | 0.26 | [5 empty] | PPA | PURPA Qualifying Facility Independent Power Producer, with special Standard Offer 2 (SO-2) type power purchase agreement to Southern California Edison | PURPA; Accelerated depreciation; Federal and state investment incentives; Solar property tax exclusion |  | Luz | USA | NextEra | NextEra | Southern California Edison |  |  | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics |  |  |  |  | 100 | 37.6 |  |  | Wet | [5 empty] | Solel | Israel | UVAC |  |  |  | 390 |  |  | Luz | USA | LS-3 | Flabeg | Germany | RP3 | 464340 | 0.96737 | [13 empty] | https://web.archive.org/web/20210921090026/https://www.eia.gov/todayinenergy/detail.php?id=49616
Solar Electric Generating Station IX |  | 9 | United States | North America | Operational | 80 | 125.04 |  | 17.84% | Parabolic Trough |  |  | Natural gas boiler |  | 1990 | California |  | Harper Dry Lake | 35.032,-117.348 | 2893 | 230 | USD | 1990 | 397.92 | 4974 | 0.27 | [5 empty] | PPA | PURPA Qualifying Facility Independent Power Producer, with special Standard Offer 2 (SO-2) type power purchase agreement to Southern California Edison | PURPA; Accelerated depreciation; Federal and state investment incentives; Solar property tax exclusion |  | Luz | USA | NextEra | NextEra | Southern California Edison |  |  | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics |  |  |  |  | 100 | 37.6 |  |  | Wet | [5 empty] | Solel | Israel | UVAC |  |  |  | 390 |  |  | Luz | USA | LS-3 | Flabeg | Germany | RP3 | 483960 | 1.0082
Saguaro Power Plant |  | 10 | United States | North America | Currently Non-Operational | 1 | 2 |  | 22.83% | Parabolic Trough |  |  |  | 2004 | 2006 | Arizona |  | Red Rock | 32.548,-111.293 | [15 empty] | 0.06 | Arizona Public Service | USA | Arizona Public Service | Arizona Public Service | Arizona Public Service | Solargenix | USA | Radco Industries | USA | Biphenyl/Diphenyl oxide: Xceltherm | Thermal oil/organics | Ormat | Israel |  | Organic Rankine | 22.2 | 20.7 |  |  | Wet | [9 empty] | 528 | 120 | 300 | Starnet | USA |  |  | LS-2 | Flabeg | Germany |  | 10340 | 1.7233 | [6 empty] | 97 | 3 | 12 | 24 | 8
Nevada Solar One |  | 11 | United States | North America | Operational | 72 | 134 |  | 21.25% | Parabolic Trough |  |  |  | 2006 | 2007 | Nevada |  | Boulder City | 35.8,-114.983 | 2625 | 266 | USD | 2007 | 315.7 | 4384.7 | 0.2 | 0.14 | USD | 2007 | 0.17 | 20 | PPA |  | 30% Federal Investment Tax Credit (ITC, 5-year MACRS) | 1.6 | Solargenix Energy (Acciona) | USA | Acciona | Acciona Solar Power | NV Energy | Lauren Engineering | USA | Dow | USA | Biphenyl/Diphenyl oxide: Dowtherm A | Thermal oil/organics | Siemens | Germany | SST-700 | [5 empty] | Wet |  | 0.5 | 0.5 hours full-load storage |  |  | Schott | Germany | PTR70 |  | 18240 | 318 | 393 | Acciona | Spain | Gossamer Space Frames | USA | SGNX-1 | Flabeg | Germany | RP2 | 357200 | 0.82685 | [5 empty] | 470 | 100 |  |  | 760 | 8 | 350 | 30
Planta Solar 10 - PS10 |  | 12 | Spain | Europe | Operational | 11 | 23.4 |  | 24.28% | Power Tower |  |  |  | 2005 | 2007 | Andalusia | Sevilla | Sanlúcar la Mayor | 37.442,-6.25 | 2076 | 35 | EUR | 2007 | 56.93 | 5175.1 | 0.21 | 0.27 | EUR | 2007 | 0.44 | 25 | FIT | Royal Decree 661/2007 | Andalusian government €1.2 million; European Commission FP5 €5 million | 0.55 | Abengoa | Spain | Abengoa | Abengoa Solar | Electric Market (Pool), Endesa Distribución (FIT) | Abener | Spain |  |  | Water | Water | GE | USA | Thermodyn |  | 45 |  |  |  | Wet | Other | 1 |  |  |  | Aalborg CSP | Denmark | Cavity | 115 |  |  |  | Abengoa | Spain | Abengoa | Spain | Solucar 120 | Flabeg | Germany |  | 75000 | 1.1364 | 624 | 120
Andasol 1 |  | 13 | Spain | Europe | Operational | 50 | 158 |  | 36.07% | Parabolic Trough |  |  |  | 2006 | 2008 | Andalusia | Granada | Aldeire y La Calahorra | 37.231,-3.071 | 2260 | 310 | EUR | 2008 | 530.93 | 10618.6 | 0.29 | 0.27 | EUR | 2008 | 0.46 | 25 | FIT | Real Decreto 661/2007 | EIB €116.7 million; European Commission 5th Framework Programme grant €5 million | 2 | Solar Millennium | Spain | ACS/Cobra 75%, 25% Solar Millennium | Cobra O&M | Endesa | Cobra 80%; Sener 20% | Spain | Dow | USA | Biphenyl/Diphenyl oxide: Dowtherm A | Thermal oil/organics | Siemens | Germany | SST-700 | Steam Rankine | 100 | 38.1 |  |  | Wet | 2-tank indirect | 7.5 | 28,500 tons of molten salt. 60% sodium nitrate, 40% potassium nitrate. 1,010 MWh. Tanks are 14 m high and 36 m in diameter. |  |  | Schott; Solel | Germany; Israel | PTR 70; UVAC 2008 |  | 11232 | 293 | 393 | UTE CT Andasol-1 (Flagsol) | Germany | SBP, Solar Milenium | Germany | SKAL ET-150 | Flabeg | Germany | RP3 | 510120 | 1.7004 | [5 empty] | 817 | 144 | 156 | 12 | 624 | 4 | 600 | 40
Jülich Solar Tower |  | 14 | Germany | Europe | Operational | 1.5 |  |  |  | Power Tower |  |  |  | 2007 | 2008 | North Rhine-Westphalia |  | Jülich | 50.915,6.388 | 902 | [14 empty] | 0.17 | Kraftanlagen München, German Aerospace Center, Solar-Institute Jülich | Germany | DLR | DLR |  | Kraftanlagen München | Germany |  |  | Air | Air | Siemens | Germany | [6 empty] | Dry | Other | 1.5 | Ceramic heat sink |  |  | Kraftanlagen München |  |  | 60 | [11 empty] | 17650 | 1.9611 | 2153 | 8
Andasol 2 |  | 15 | Spain | Europe | Operational | 50 | 158 |  | 36.07% | Parabolic Trough |  |  |  | 2007 | 2009 | Andalusia | Granada | Aldeire y La Calahorra | 37.231,-3.071 | 2260 | 300 | EUR | 2009 | 483.29 | 9665.7 | 0.26 | 0.27 | EUR | 2009 | 0.43 | 25 | FIT | Real Decreto 661/2007 | EIB €112.5 million | 2 | Solar Millennium | Spain | ACS/Cobra 75%, 25% Solar Millennium | Cobra O&M | Endesa | Cobra 80%; Sener 20% | Spain | Dow | USA | Biphenyl/Diphenyl oxide: Dowtherm A | Thermal oil/organics | Siemens | Germany | SST-700 | Steam Rankine | 100 | 38.1 |  |  | Wet | 2-tank indirect | 7.5 | 28,500 tons of molten salt. 60% sodium nitrate, 40% potassium nitrate. 1,010 MWh. Tanks are 14 m high and 36 m in diameter. |  |  | Schott | Germany |  |  | 11232 | 293 | 393 | Flagsol | Germany | SBP, Solar Milenium | Germany | SKAL ET-150 | Flabeg | Germany | RP3 | 510120 | 1.7004 | [5 empty] | 817 | 144 | 156 | 12 | 624 | 4 | 600 | 40
Holaniku at Keahole Point |  | 16 | United States | North America | Currently Non-Operational | 2 | 4 |  | 22.83% | Parabolic Trough |  |  |  | 2006 | 2009 | Hawaii |  | Keahole Point | 19.717,-156.033 | [15 empty] | 0.01 | Keahole Solar Power, LLC, Sopogy | USA | Keahole Solar Power, LLC | Sopogy, Inc. | HELCO |  |  | Radco Industries | USA | Biphenyl/Diphenyl oxide: Xceltherm | Thermal oil/organics |  |  |  | Steam Rankine |  |  |  |  | Wet | Other | 2 | [8 empty] | 93 | 176 |  |  | Sopogy | USA | SopoNova | [14 empty] | 1008
Ibersol Ciudad Real (Puertollano) |  | 17 | Spain | Europe | Operational | 50 | 103 |  | 23.52% | Parabolic Trough |  |  |  | 2007 | 2009 | Castilla-La Mancha | Ciudad Real | Puertollano | 38.643,-3.975 | 2042 | 200 | EUR | 2009 | 322.19 | 6443.8 | 0.27 | 0.27 | EUR | 2009 | 0.43 | 25 | FIT |  |  | 1.5 | Iberdrola | Spain | 90% Iberdola; IDAE 10% | Iberdrola Renovables | Market | Iberdrola Renovables | Spain | Dow | USA | Biphenyl/Diphenyl oxide: Dowtherm A | Thermal oil/organics | Siemens | Germany |  | Steam Rankine | 100 | 38.9 |  |  | Wet | [5 empty] | Schott, Solel | Germany; Israel |  |  | 6336 | 304 | 391 | Iberdrola | Spain | Iberdrola | Spain | ET-150 | Flabeg, Rioglass | Germany, Spain |  | 287760 | 0.9592 | [7 empty] | 88 | 12 | 352 | 4 |  | 60
La Risca - Alvarado I |  | 18 | Spain | Europe | Operational | 50 | 105 |  | 23.97% | Parabolic Trough |  |  |  | 2007 | 2009 | Extremadura | Badajoz | Alvarado | 38.827,-6.826 | 2085 | 230 | EUR | 2009 | 370.52 | 7410.4 | 0.3 | 0.27 | EUR | 2009 | 0.43 | 25 | FIT | Real Decreto 661/2007 |  | 1.35 | Acciona | Spain | Acciona | Acciona Energía |  | Acciona, IDOM | Spain |  |  | Biphenyl/Diphenyl oxide | Thermal oil/organics | Siemens | Germany | SST-700 | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany |  |  |  | 293 | 393 | Acciona | Spain | Gossamer Space Frames | USA | SGNX-2 | Flabeg | Germany | RP2 | 352854 | 1.1762 | [7 empty] | 96 |  | 768 | 8 | 350 | 31
Planta Solar 20 - PS20 |  | 19 | Spain | Europe | Operational | 20 | 48 |  | 27.4% | Power Tower |  |  |  | 2006 | 2009 | Andalusia | Sevilla | Sanlúcar la Mayor | 37.442,-6.25 | 2076 | 90 | EUR | 2009 | 144.99 | 7249.3 | 0.26 | 0.27 | EUR | 2009 | 0.43 | 25 | FIT | Royal Decree 661/2007 | Andalusian government €1.2 million | 0.8 | Abengoa | Spain | Abengoa | Abengoa Solar | Electric Market (Pool), Endesa Distribución (FIT) | Abener | Spain |  |  | Water | Water | Franco Tosi | Italy |  |  | 45 |  |  |  | Wet | Other | 1 |  |  |  | Aalborg CSP | Denmark | Cavity | 165 |  |  |  | Abengoa | Spain | Abengoa | Spain | Solucar 120 |  |  |  | 150000 | 1.25 | 1255 | 120
Puerto Errado 1 Thermosolar Power Plant |  | 20 | Spain | Europe | Operational | 1.4 | 2 |  | 16.31% | Linear Fresnel |  |  |  | 2008 | 2009 | Región de Murcia | Murcia | Calasparra | 38.278,-1.6 | [7 empty] | 0.27 | EUR | 2009 | 0.43 | 25 |  | b1.2 R.D 661/2007 |  | 0.05 | Novatec Solar GmbH | Spain, Germany | Novatec Solar España S.L. | Novatec Solar España S.L., Power Support | Iberdrola S.A.U., REE | Novatec Solar España S.L. | Spain |  |  | Water | Water | KKK-Siemens | Germany |  |  | 55 |  |  |  | Dry | Single-tank thermocline |  | Ruths tank |  |  | Novatec | Spain | Nova-1 |  |  | 140 | 270 | [5 empty] | Novatec Solar España S.L. | Spain | [5 empty] | 16 | 2 | 806 | [7 empty] | 1
Solnova 1 |  | 21 | Spain | Europe | Operational | 50 | 113.52 |  | 25.92% | Parabolic Trough |  |  |  | 2007 | 2009 | Andalusia | Sevilla | Sanlúcar la Mayor | 37.442,-6.25 | 2076 | 250 | EUR | 2009 | 402.74 | 8054.8 | 0.3 | 0.27 | EUR | 2009 | 0.43 | 25 | FIT | Royal Decree 661/2007 | EIB for Solnova 1 and 3: €129 million | 1.15 | Abengoa | Spain | Abengoa | Abengoa | Electrical Market (Pool), Endesa Distribution (FIT) | Abener | Spain |  |  | Thermal oil | Thermal oil/organics |  |  |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany |  |  | 12960 |  | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) | Rioglass | Spain |  | 300000 | 1 | [5 empty] | 833 | 150 | 90 |  | 360 | 4
Solnova 3 |  | 22 | Spain | Europe | Operational | 50 | 113.52 |  | 25.92% | Parabolic Trough |  |  |  | 2007 | 2009 | Andalusia | Sevilla | Sanlúcar la Mayor | 37.442,-6.25 | 2076 | 250 | EUR | 2009 | 402.74 | 8054.8 | 0.3 | 0.27 | EUR | 2009 | 0.43 | 25 | FIT | Royal Decree 661/2007 | EIB for Solnova 1 and 3: €129 million | 1.15 | Abengoa | Spain | Abengoa | Abengoa | Electrical Market (Pool), Endesa Distribution (FIT) | Abener | Spain |  |  | Thermal oil | Thermal oil/organics |  |  |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany |  |  | 12960 |  | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) | Rioglass | Spain |  | 300000 | 1 | [5 empty] | 833 | 150 | 90 |  | 360 | 4
Solnova 4 |  | 23 | Spain | Europe | Operational | 50 | 113.52 |  | 25.92% | Parabolic Trough |  |  |  | 2008 | 2009 | Andalusia | Sevilla | Sanlúcar la Mayor | 37.442,-6.25 | 2076 | 210 | EUR | 2009 | 338.3 | 6766 | 0.26 | 0.27 | EUR | 2009 | 0.43 | 25 | FIT | Royal Decree 661/2007 |  | 1.15 | Abengoa | Spain | Abengoa | Abengoa | Electrical Market (Pool), Endesa Distribution (FIT) | Abener | Spain |  |  | Thermal oil | Thermal oil/organics |  |  |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany |  |  | 12960 |  | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) | Rioglass | Spain |  | 300000 | 1 | [5 empty] | 833 | 150 | 90 |  | 360 | 4
Archimede |  | 24 | Italy | Europe | Operational | 4.7 | 9.2 |  | 22.35% | Parabolic Trough |  |  |  | 2008 | 2010 | Andalusia |  | Priolo Gargallo | 37.134,15.217 | 1936 | [14 empty] | 0.08 | ENEL | Italy | ENEL | ENEL | [5 empty] | Molten salt (60% NaNO?, 40% KNO?) | Salt | Tosi | Italy |  |  | 93.8 | 39.3 |  |  | wet | 2-tank direct | 8 | Total of 1,580 tons of molten salt. 60% sodium nitrate, 40% potassium nitrate. Capacity 100 MWh (thermal). Tanks are 6.5 m high and 13.5 m in diameter. |  |  | Archimede Solar Energy |  |  |  | 1296 | 290 | 550 |  |  | COMES |  |  | Ronda Reflex | Italy |  | 31860 | 1.1298 | [5 empty] | 590 | 100 | 9 | 8 | 54 | 6
Extresol 1 |  | 25 | Spain | Europe | Operational | 50 | 158 |  | 36.07% | Parabolic Trough |  |  |  | 2009 | 2010 | Extremadura | Badajoz | Torre de Miguel Sesmero | 38.65,-6.733 | 2096 | 300 | EUR | 2010 | 454.48 | 9089.6 | 0.25 | 0.27 | EUR | 2010 | 0.41 | 25 | FIT | Real Decreto 661/2007 |  | 2 | Cobra | Spain | FCC Energy | Cobra O&M | Endesa | Cobra, Sener | Spain |  |  | Biphenyl/Diphenyl oxide | Thermal oil/organics | Siemens | Germany |  | Steam Rankine | 100 | 38.1 |  |  | Wet | 2-tank indirect | 7.5 | 28,500 tons of molten salt. 60% sodium nitrate, 40% potassium nitrate. 1,010 MWh. Tanks are 14 m high and 36 m in diameter. |  |  | Schott | Germany | PTR 70 |  | 22464 | 293 | 393 | UTE CT Extresol-1: Cobra (80%) and Sener (20% | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 510120 | 1.7004 | [5 empty] | 817 | 144 | 156 | 12 | 624 | 4 | 600 | 40
Extresol 2 |  | 26 | Spain | Europe | Operational | 50 | 158 |  | 36.07% | Parabolic Trough |  |  |  | 2009 | 2010 | Extremadura | Badajoz | Torre de Miguel Sesmero | 38.65,-6.733 | 2096 | 300 | EUR | 2010 | 454.48 | 9089.6 | 0.25 | 0.27 | EUR | 2010 | 0.41 | 25 | FIT | Real Decreto 661/2007 |  | 2 | Cobra | Spain | FCC Energy | Cobra O&M | Endesa | Cobra | Spain |  |  | Biphenyl/Diphenyl oxide | Thermal oil/organics | Siemens | Germany |  |  | 100 | 38.1 |  |  | Wet | 2-tank indirect | 7.5 | 28,500 tons of molten salt. 60% sodium nitrate, 40% potassium nitrate. 1,010 MWh. Tanks are 14 m high and 36 m in diameter. |  |  | Solel | Israel | UVAC-2008 |  | 22464 | 293 | 393 | Cobra | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 510120 | 1.7004 | [5 empty] | 817 | 144 | 156 | 12 | 624 | 4 | 600 | 40
La Florida |  | 27 | Spain | Europe | Operational | 50 | 175 |  | 39.95% | Parabolic Trough |  |  |  | 2008 | 2010 | Extremadura | Badajoz | Badajoz | 38.817,-6.829 | 2086 | 319 | EUR | 2010 | 483.27 | 9665.3 | 0.24 | 0.27 | EUR | 2010 | 0.41 | 25 | FIT |  |  | 2 | Renovables SAMCA | Spain | Renovables SAMCA | Renovables SAMCA |  | Renovables SAMCA | Spain | Dow | USA | Biphenyl/Diphenyl oxide | Thermal oil/organics | Siemens | Germany | SST 800 | Steam Rankine | 100 | 38.1 |  |  | Wet | 2-tank indirect | 7.5 | 29,000 tons of molten salt. 60% sodium nitrate, 40% potassium nitrate. |  |  | Schott | Germany |  |  | 24192 | 298 | 393 | Ingemetal | Spain | SAMCA | Spain | SAMCA-Trough | Rioglass | Spain |  | 552750 | 1.8425 | [5 empty] | 822 | 150 | 168 | 12 | 672 | 4 | 950 | 45
Majadas I |  | 28 | Spain | Europe | Operational | 50 | 104.5 |  | 23.86% | Parabolic Trough |  |  |  | 2009 | 2010 | Extremadura | Cáceres | Majadas de Tiétar | 39.968,-5.742 | 2086 | 237 | EUR | 2010 | 359.04 | 7180.8 | 0.3 | 0.27 | EUR | 2010 | 0.41 | 25 | FIT | RD 661/2007 |  | 1.35 | Acciona | Spain | Acciona | Acciona Energía |  | Acciona, IDOM | Spain |  |  | Biphenyl/Diphenyl oxide | Thermal oil/organics | GE |  |  | Steam Rankine |  |  |  |  | Wet | [5 empty] | Schott | Germany |  |  |  |  | 393 | Acciona | Spain | Gossamer Space Frames | USA | SGNX-2 | Rioglass | Spain |  | 372240 | 1.2408 | [5 empty] | 470 | 100 | 99 | 12 | 792 | 8 | 350 | 31
Maricopa Solar Project |  | 29 | United States | North America | Currently Non-Operational | 1.5 |  |  |  | Dish |  |  |  | 2009 | 2010 | Arizona |  | Peoria | 33.559,-112.219 | [15 empty] | 0.06 | Tessera Solar | USA | Tessera Solar | Tessera Solar | Salt River Project (SRP) | Mortenson Construction | [8 empty] | Stirling |  |  |  |  | - | [14 empty] | Stirling Energy Systems (SES) | SunCatcher (Dish) 25KW | [6 empty] | 60 | [10 empty] | 50 | 5
Martin Next Generation Solar Energy Center |  | 30 | United States | North America | Operational | 75 | 155 |  | 23.59% | Hybrid; Trough |  |  | Natural gas boiler | 2009 | 2010 | Florida |  | Indiantown | 27.054,-80.563 | 1799 | 476.3 | USD | 2010 | 543.6 | 7248 | 0.3 | [7 empty] | Federal tax investment credit $120 million | 2.02 | Florida light and power | USA | Florida light and power | Florida Power & Light Co. | Florida Power & Light Co. | Lauren Engineering | USA | Dow | USA | Biphenyl/Diphenyl oxide: Dowtherm A | Thermal oil/organics |  |  |  | Steam Rankine |  |  |  |  | Wet | [5 empty] | Solel | Israel | UVAC-2008 | [6 empty] | Gossamer Space Frames | USA | LAT 1 | Rioglass | Spain |  | 464908 | 1.0331 | [6 empty] | 72 | 142 | 6 | 1136 | 8
Palma del Río II |  | 31 | Spain | Europe | Operational | 50 | 115.5 |  | 26.37% | Parabolic Trough |  |  |  | 2008 | 2010 | Andalusia | Córdoba | Palma del Río | 37.645,-5.258 | 2064 | 247 | EUR | 2010 | 374.19 | 7483.8 | 0.28 | 0.27 | EUR | 2010 | 0.41 | 25 | FIT | RD 661/2007 |  | 1.35 | Acciona | Spain | Acciona | Acciona Energía |  | Acciona | Spain |  |  | Biphenyl/Diphenyl oxide | Thermal oil/organics | GE | USA |  | Steam Rankine |  |  |  |  | Wet | [5 empty] | Acciona | Spain |  |  |  |  | 393 | Acciona | Spain | Gossamer Space Frames | USA | SGNX-2 | Guardian | USA |  | 372240 | 1.2408 | [5 empty] | 470 | 100 | 99 | 12 | 792 | 8 | 350 | 31
ACME Solar Tower |  | 32 | India | Asia | Operational | 2.5 |  |  |  | Power Tower |  |  |  |  | 2011 | Rajasthan |  | Bikaner | 28.184,73.241 | [15 empty] | 0.05 | ACME Group, eSolar | USA | ACME Group | ACME Group | [5 empty] | Water | Water | MaxWatt | India |  | Steam Rankine | 60 |  |  |  | Wet | [14 empty] | eSolar | USA |  |  |  |  | 16222 | 1.0815 | 14280 | 1
Andasol 3 |  | 33 | Spain | Europe | Operational | 50 | 175 |  | 39.95% | Parabolic Trough |  |  |  | 2008 | 2011 | Andalusia | Granada | Aldeire y La Calahorra | 37.229,-3.069 | 2260 | 315 | EUR | 2011 | 490.56 | 9811.2 | 0.24 | 0.27 | EUR | 2011 | 0.42 | 25 | FIT |  |  | 2 | Solar Millennium (Ferrostaal) | Germany | Ferrostaal, Solar Millennium, RWE |  |  | MAN Solar Millennium; Duro Felguera | Germany; Spain |  |  | Thermal Oil | Thermal oil/organics | MAN Turbo | Germany |  | Steam Rankine | 100 |  |  |  | Wet | 2-tank indirect | 7.5 | Molten salts |  |  | Schott | Germany |  |  |  | 293 | 393 | Flagsol | Germany | SBP, Solar Milenium | Germany | SKAL ET-150 | Rioglass | Spain |  | 510120 | 1.7004 | [5 empty] | 817 | 150 | 156 | 12 | 624 | 4
Arcosol 50 (Valle I) |  | 34 | Spain | Europe | Operational | 50 | 175 |  | 39.95% | Parabolic Trough |  |  |  | 2009 | 2011 | Andalusia | Cádiz | San José del Valle | 36.661,-5.833 | 2007 | 270 | EUR | 2011 | 420.48 | 8409.6 | 0.21 | 0.27 | EUR | 2011 | 0.42 | 25 | FIT |  |  | 2.3 | Torresol | Spain, UAE | Torresol (Sener & Masdar) | Torresol |  | UTE Valle I | Spain |  |  | Biphenyl/Diphenyl oxide | Thermal oil/organics |  |  |  | Steam Rankine | 100 | 38.1 |  |  | Wet | 2-tank indirect | 7.5 | 28,500 tons of molten salt. 60% sodium nitrate, 40% potassium nitrate. |  |  | Sener | Spain |  |  |  | 293 | 393 | Sener | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 510120 | 1.7004 | [5 empty] | 817 |  | 156 |  | 624 | 4 | 900 | 45
Gemasolar Thermosolar Plant / Solar TRES |  | 35 | Spain | Europe | Operational | 20 | 110 |  | 62.79% | Power Tower |  |  |  | 2009 | 2011 | Andalusia | Sevilla | Fuentes de Andalucía | 37.562,-5.33 | 2072 | 230 | EUR | 2011 | 358.19 | 17909.3 | 0.28 | 0.27 | EUR | 2011 | 0.42 | 25 | FIT |  | EIB €110 million; ICO €16.14 million | 1.95 | Torresol | Spain | Masdar, Sener | Torresol O&M |  | UTE Solar Tres | Spain |  |  | Molten salts (sodium and potassium nitrates) | Salt | Siemens | Germany | SST-600 | Steam Rankine |  |  |  |  | Wet | 2-tank direct | 15 | One cold-salts tank (290ºC) from where salts are pumped to the tower receiver and heated up to 565ºC, to be stored in one hot-salts tank (565ºC). Annual equivalent hours = 5,000. |  |  | ITP JV: Sener, Rolls Royce | Spain |  | 140 |  |  |  | Sener | Spain | Sener | Spain | HE54 | Guardian | USA |  | 304750 | 2.5396 | 2650 | 120 | [9 empty] | 800 | 45
Helioenergy 1 |  | 36 | Spain | Europe | Operational | 50 | 95 |  | 21.69% | Parabolic Trough |  |  |  |  | 2011 | Andalusia | Sevilla | Écija | 37.582,-5.116 | 2159 | 240 | EUR | 2011 | 373.76 | 7475.2 | 0.34 | 0.27 | EUR | 2011 | 0.42 | 25 | FIT | Real Decreto 661/2007 |  | 1.1 | Abengoa Solar, EON | Spain | Abengoa, Eon | Abengoa, EON |  | Abener, Teyma | Spain |  |  | Thermal Oil | Thermal oil/organics | Siemens | Germany | SST-700 | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany |  |  | 12960 | 293 | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) |  |  |  | 300000 | 1 | [6 empty] | 150 | 90 | 12 | 360 | 4 | 600 | 60
ISCC Ain Beni Mathar |  | 37 | Morocco | MENA | Operational | 20 | 55 |  | 31.39% | ISCC; Trough | 472 | 23.6 | ISCC | 2008 | 2011 | Oriental | Ain Beni Mathar | Ain Beni Mathar | 34.064,-2.1 | 2072 | [6 empty] | 0.24 | USD | 2011 | 0.27 | 25 | PPA |  | Global Environment Facility (GEF; World Bank) $43 million; AfDB €136 million in 2005 & €151.14 million in 2008; ONEE received loan from Spanish Institute de Credito Oficial (ICO) €100 million in 2009 |  | Abengoa | Spain | Abengoa, ONE | Abengoa Solar / ONE | ONE (Office National de l'Electricite) | Abener | Spain | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics |  |  |  | Steam Rankine |  |  |  |  | Wet | [5 empty] | Schott | Germany | PTR 70 |  | 8064 |  | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) | Rioglass | Spain |  | 183120 | 1.526 | [6 empty] | 150 | 56 |  | 224 | 4
ISCC Hassi R'mel |  | 38 | Algeria | MENA | Operational | 20 |  |  |  | ISCC; Trough | 130 | 6.5 | ISCC | 2007 | 2011 | Laghouat | Hassi R'mel | Hassi R'mel | 33.124,3.357 | 2159 | [10 empty] | 25 | PPA |  | IFC (World bank group) $15 million; International Bank for Reconstruction and Development (IBRD) $15 million, AfDB $15 million. | 0.64 | Abengoa | Spain | Abener | Abener | Sonatrach | Abener | Spain |  |  | Thermal oil | Thermal oil/organics | Siemens | Germany | SST-900 | Steam Rankine |  |  |  |  | Dry | [5 empty] | Schott | Germany | PTR 70 |  | 8064 | 293 | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) | Rioglass | Spain |  | 183860 | 1.5322 | [6 empty] | 150 | 56 |  | 224 | 4
ISCC Kuraymat |  | 39 | Egypt | MENA | Operational | 20 | 34 |  | 19.41% | ISCC; Trough | 150 | 7.5 | ISCC |  | 2011 |  |  | Kuraymat | 29.279,31.249 | 2154 | [11 empty] | PPA |  | Egyptian National Renewable Energy Agency $100 million; GEF $50 million; Japanese Bank for International Development $190 million |  | NREA | Egypt | NREA |  |  | Orascom, Flagsol | Spain | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics | Siemens | Germany | SST-900 | Steam Rankine |  |  |  |  | Wet | [5 empty] | Schott | Germany | PTR 70 |  |  | 293 | 393 | Flagsol | Germany | SBP, Solar Milenium | Germany | SKAL ET-150 | Flabeg | Germany | RP3 | 130800 | 1.09 | [7 empty] | 40 | 12 | 160 | 4
La Dehesa |  | 40 | Spain | Europe | Operational | 50 | 175 |  | 39.95% | Parabolic Trough |  |  |  | 2008 | 2011 | Extremadura | Badajoz | La Garrovilla | 38.952,-6.463 | 2069 | 309 | EUR | 2011 | 481.22 | 9624.3 | 0.24 | 0.27 | EUR | 2011 | 0.42 | 25 | FIT |  |  | 2 | Renovables SAMCA | Spain | Renovables SAMCA | Renovables SAMCA |  | Renovables SAMCA | Spain |  |  | Biphenyl/Diphenyl oxide | Thermal oil/organics | Siemens | Germany | SST-700 | Steam Rankine | 100 | 38.1 |  |  | Wet | 2-tank indirect | 7.5 | 29,000 tons of molten salt. 60% sodium nitrate, 40% potassium nitrate. |  |  | Schott | Germany | PTR 70 |  | 24192 | 298 | 393 | Ingemetal | Spain | SAMCA | Spain | SAMCA-Trough | Rioglass | Spain |  | 552750 | 1.8425 | [5 empty] | 822 | 150 | 168 | 12 | 672 | 4 | 950 | 45
Lake Cargelligo |  | 41 | Australia | Australia | Currently Non-Operational | 3 |  |  |  | Power Tower |  |  |  |  | 2011 | New South Wales |  | Lake Cargelligo | -33.312,146.41 | [14 empty] | AUD 5$ million grant as a part of AEST Program |  | Lloyd Energy Systems Pty Ltd | Australia | Graphite Energy | Graphite Energy | Australian National Energy Market | Comet Windmills |  |  |  | Water | Water |  |  |  | Steam Rankine | 50 |  |  |  |  | Other |  | Core graphite thermal storage technology |  |  | Lloyd Energy Systems Pty Ltd |  | Graphite solar storage receiver | [12 empty] | 6080 | 0.33778 | 620 | 10
Lebrija 1 |  | 42 | Spain | Europe | Operational | 50 | 120 |  | 27.4% | Parabolic Trough |  |  |  | 2008 | 2011 | Andalusia | Sevilla | Lebrija | 37.003,-6.048 | 2065 | 303 | EUR | 2011 | 471.87 | 9437.4 | 0.34 | 0.27 | EUR | 2011 | 0.42 | 25 | FIT |  |  | 1.88 | Solucia | Spain | Solel 50%, Valoriza 50% | Soleval Renovables, S.L. |  | Soleval Renovables | Spain | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics | Siemens | Germany | SST-700 | Steam Rankine | 100 | 38.7 |  |  | Wet | [5 empty] | Solel | Israel | UVAC-2010 |  | 18144 |  | 395 |  |  | Solel | Israel | SunField 6 | Guardian | USA | EcoGuard Solar Boost | 412020 | 1.3734 | [5 empty] | 545 | 95 |  |  | 756 |  | 500
Manchasol 1 |  | 43 | Spain | Europe | Operational | 50 | 158 |  | 36.07% | Parabolic Trough |  |  |  | 2008 | 2011 | Castilla-La Mancha | Ciudad Real | Alcázar de San Juan | 39.188,-3.309 | 2107 | 300 | EUR | 2011 | 467.2 | 9344 | 0.25 | 0.27 | EUR | 2011 | 0.42 | 25 | FIT |  | EIB €58 million; KfW 45 million Euro loan | 2 | Cobra | Spain | ACS/Cobra | Cobra O&M | Unión Fenosa | Cobra | Spain |  |  | Biphenyl/Diphenyl oxide | Thermal oil/organics | Siemens | Germany |  |  | 100 | 38.1 |  |  | Wet | 2-tank indirect | 7.5 | 28,500 tons of molten salt. 60% sodium nitrate, 40% potassium nitrate. 375 MWh. Tanks are 14 m high and 36 m in diameter. |  |  | Schott, Solel | Germany; Israel |  |  | 11232 | 293 | 393 | Cobra | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 510120 | 1.7004 | [5 empty] | 817 | 144 | 156 | 12 | 624 | 4 | 600 | 40
Manchasol 2 |  | 44 | Spain | Europe | Operational | 50 | 159 |  | 36.3% | Parabolic Trough |  |  |  | 2009 | 2011 | Castilla-La Mancha | Ciudad Real | Alcázar de San Juan | 39.182,-3.314 | 2107 | 300 | EUR | 2011 | 467.2 | 9344 | 0.25 | 0.27 | EUR | 2011 | 0.42 | 25 | FIT |  | EIB €58 million; KfW 45 million Euro loan | 2 | Cobra | Spain | ACS/Cobra | Cobra O&M | Unión Fenosa | Cobra | Spain |  |  | Biphenyl/Diphenyl oxide | Thermal oil/organics | Siemens | Germany |  |  | 100 | 38.1 |  |  | Wet | 2-tank indirect | 7.5 | 28,500 tons of molten salt. 60% sodium nitrate, 40% potassium nitrate. 375 MWh. Tanks are 14 m high and 36 m in diameter. |  |  | Schott | Germany |  |  | 11232 | 293 | 393 | Cobra | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 510120 | 1.7004 | [5 empty] | 817 | 144 | 156 | 12 | 624 | 4 | 600 | 40
Palma del Río I |  | 45 | Spain | Europe | Operational | 50 | 114.5 |  | 26.14% | Parabolic Trough |  |  |  | 2009 | 2011 | Andalusia | Córdoba | Palma del Río | 37.645,-5.258 | 2064 | 247 | EUR | 2011 | 384.66 | 7693.2 | 0.29 | 0.27 | EUR | 2011 | 0.42 | 25 | FIT | RD 661/2007 |  | 1.35 | Acciona | Spain | Acciona | Acciona Energía |  | Acciona | Spain |  |  | Biphenyl/Diphenyl oxide | Thermal oil/organics | GE | USA |  | Steam Rankine |  |  |  |  | Wet | [5 empty] | Acciona | Spain |  |  |  |  | 393 | Acciona | Spain | Gossamer Space Frames | USA | SGNX-2 | Flabeg | Germany | RP2 | 372240 | 1.2408 | [5 empty] | 470 | 100 | 99 | 12 | 792 | 8 | 350 | 31
Termesol 50 |  | 46 | Spain | Europe | Operational | 50 | 175 |  | 39.95% | Parabolic Trough |  |  |  | 2009 | 2011 | Andalusia | Cádiz | San José del Valle | 36.661,-5.847 | 2007 | 270 | EUR | 2011 | 420.48 | 8409.6 | 0.21 | 0.27 | EUR | 2011 | 0.42 | 25 | FIT |  |  | 2.3 | Torresol | Spain, UAE | Torresol (Sener, Masdar) | Torresol |  | Sener | Spain |  |  | Biphenyl/Diphenyl oxide | Thermal oil/organics |  |  |  | Steam Rankine | 100 | 38.1 |  |  | Wet | 2-tank indirect | 7.5 | 28,500 tons of molten salt. 60% sodium nitrate, 40% potassium nitrate. |  |  | Schott | Germany |  |  |  | 293 | 393 | Sener | Spain | Sener | Spain | SenerTrough2 | Flabeg | Germany | RP3 | 510120 | 1.7004 | [5 empty] | 817 |  | 156 |  | 624 | 4 | 900 | 45
Aste 1A |  | 47 | Spain | Europe | Operational | 50 | 170 |  | 38.81% | Parabolic Trough |  |  |  | 2011 | 2012 | Castilla-La Mancha | Ciudad Real | Alcázar de San Juan | 39.176,-3.234 | 2104 | 237.5 | EUR | 2012 | 335.27 | 6705.4 | 0.17 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 1.8 | Elecnor, Aries | Spain | Elcnor, Aries, ABM Amro |  |  | Elecnor | Spain | Dow | USA | Biphenyl/Diphenyl oxide: Dowtherm A | Thermal oil/organics |  |  |  | Steam Rankine | 100 |  |  |  | Wet | 2-tank indirect | 8 | Molten salts; 60% Sodium Nitrate, 40% Potassium Nitrate |  |  | Siemens | Germany | UVAC-2010 |  | 22464 | 293 | 393 | Sener | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 510120 | 1.7004 | [5 empty] | 817 | 150 | 156 | 12 | 624 | 4 | 500 | 50
Aste 1B |  | 48 | Spain | Europe | Operational | 50 | 170 |  | 38.81% | Parabolic Trough |  |  | HTF Boiler | 2011 | 2012 | Castilla-La Mancha | Ciudad Real | Alcázar de San Juan | 39.173,-3.267 | 2104 | 237.5 | EUR | 2012 | 335.27 | 6705.4 | 0.17 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 1.7 | Elecnor, Aries | Spain | Elcnor, Aries, ABM Amro |  |  | Elecnor | Spain | Dow | USA | Biphenyl/Diphenyl oxide: Dowtherm A | Thermal oil/organics |  |  |  | Steam Rankine | 100 |  |  |  | Wet | 2-tank indirect | 8 | 60% Sodium Nitrate, 40% Potassium Nitrate. 1,010 MWht |  |  | Siemens | Germany | UVAC-2010 |  | 17280 | 293 | 393 | Sener | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 510120 | 1.7004 | [6 empty] | 150 | 120 | 12 | 480 | 4 | 500 | 50
Astexol II |  | 49 | Spain | Europe | Operational | 50 | 170 |  | 38.81% | Parabolic Trough |  |  |  | 2010 | 2012 | Extremadura | Badajoz | Olivenza | 38.81,-7.053 | 2055 | 225 | EUR | 2012 | 317.63 | 6352.5 | 0.16 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 1.6 | Elecnor, Aries | Spain | Elcnor, Aries, ABM Amro |  |  | Elecnor | Spain |  |  | Thermal Oil | Thermal oil/organics |  |  |  | Steam Rankine | 100 |  |  |  | Wet | 2-tank indirect | 8 | 60% Sodium Nitrate, 40% Potassium Nitrate | [7 empty] | 293 | 393 | Flagsol | Germany | Flagsol, SBP | Germany | SKAL ET-150 |  |  |  | 510120 | 1.7004 | [5 empty] | 817 | 149 | 156 | 12 | 624 | 4 | 500 | 50
Augustin Fresnel 1 |  | 50 | France | Europe | Operational | 0.3 |  |  |  | Linear Fresnel |  |  |  | 2011 | 2012 | Occitanie |  | Targassonne | 42.501,1.972 | 1800 | [13 empty] | French Goverment Co-funding | 0.01 | Solar Euromed | France | Solar Euromed | Solar Euromed |  | Solar Euromed |  |  |  | Water | Water |  |  |  | Steam Rankine | 100 |  |  |  | Dry | Other | 0.25 | Ruths tank |  |  | Solar Euromed | France | AF1 |  |  |  | 300 | [5 empty] | Solar Euromed | France |  | 400 | 0.22222 |  |  |  | 1 | 40 | [6 empty] | 10 | 3
Borges Termosolar |  | 51 | Spain | Europe | Operational | 22.5 | 44.1 |  | 22.37% | Biomass-Hybrid; Trough | 44 | 1.9556 | Biomass (2x22MWt) | 2011 | 2012 | Catalonia | Lleida | Les Borges Blanques | 41.529,0.8 | 1878 | 153 | EUR | 2012 | 215.99 | 9599.4 | 0.42 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 0.96 | Abantia | Spain | Abantia, Comsa |  |  | Abantia & Comsa | Spain |  |  | Thermal Oil | Thermal oil/organics | MAN Turbo | Germany |  | Steam Rankine |  | 37 |  |  | Wet | [5 empty] | Siemens | Germany | UVAC-2010 |  | 8064 | 293 | 393 | Siemens | Germany | Solel | Israel | SunField 6 |  |  |  | 183120 | 1.3564 | [5 empty] | 545 | 96 | 56 | 8 | 336 | 6 |  | 30
Badaling Dahan 1 MW Tower | 延庆八达岭太阳能热发电实验电站 | 52 | China | Asia | Operational | 1 | 1.9 |  | 21.69% | Power Tower |  |  | Oil boiler | 2009 | 2012 | Beijing | Yanqing | Badaling | 40.382,115.938 | 1290 | [12 empty] | “11th Five-Year plan" (863 program) |  | 0.05 | Institute of Electrical Engineering of CAS | China | Institute of Electrical Engineering of CAS | Institute of Electrical Engineering of Chinese Academy of Sciences |  | Institute of Electrical Engineering of CAS | China |  |  | Water | Water | Hangzhou Steam Turbine Company | China |  | Steam Rankine |  |  |  |  | Wet (Closed water) | Other | 1 | Two stages: saturated steam/oil |  |  | Dongfang | China | Cavity Receiver (5x5 m) | 118 |  |  |  | Himin Solar | China | Himin Solar | China |  | Taishan Huayue | China |  | 10000 | 1.6667 | 100 | 100
Extresol 3 |  | 53 | Spain | Europe | Operational | 50 | 158 |  | 36.07% | Parabolic Trough |  |  |  | 2009 | 2012 | Extremadura | Badajoz | Torre de Miguel Sesmero | 38.65,-6.733 | 2096 | 390 | USD | 2012 | 428.21 | 8564.3 | 0.23 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 2 | Cobra | Spain | FCC Energy | Cobra O&M | Endesa | Cobra | Spain | Dow | USA | Biphenyl/Diphenyl oxide: Dowtherm A | Thermal oil/organics | Siemens | Germany |  |  | 100 | 38.1 |  |  | Wet | 2-tank indirect | 7.5 | 28,500 tons of molten salt. 60% sodium nitrate, 40% potassium nitrate. 1,010 MWh. Tanks are 14 m high and 36 m in diameter. |  |  | Solel | Israel | UVAC-2008 |  | 22464 | 293 | 393 | Cobra | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 510120 | 1.7004 | [5 empty] | 817 | 144 | 156 | 12 | 624 | 4 | 600 | 40
Greenway CSP Mersin Tower Plant |  | 54 | Turkey | Europe | Operational | 1.4 |  |  |  | Power Tower |  |  |  |  | 2012 |  |  | Mersin | 36.865,34.61 | [16 empty] | Greenway CSP | Turkey | Greenway CSP | Greenway CSP | [5 empty] | Water | Water |  |  |  | Steam Rankine | 55 |  |  |  |  | Other |  | Molten salt. Single 3-phase tank, natural circulation, super steam junction design
Guzmán |  | 55 | Spain | Europe | Operational | 50 | 104 |  | 23.74% | Parabolic Trough |  |  |  | 2010 | 2012 | Andalusia | Córdoba | Palma del Río | 37.152,-5.271 | 2064 | 272 | EUR | 2012 | 383.98 | 7679.5 | 0.32 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 2 | FCC Energy | Spain | FCC Energy, Mitsui |  |  | FCC, Abantia, IDOM | Spain | Dow | USA | Biphenyl/Diphenyl oxide: Dowtherm A | Thermal oil/organics | MAN Turbo | Germany |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany | PTR 70 |  | 13824 | 293 | 393 | Sener | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 310406 | 1.0347 | [5 empty] | 817 | 150 | 96 | 12 | 384 | 4
Helioenergy 2 |  | 56 | Spain | Europe | Operational | 50 | 95 |  | 21.69% | Parabolic Trough |  |  |  |  | 2012 | Andalusia | Sevilla | Écija | 37.582,-5.116 | 2068 | 240 | EUR | 2012 | 338.8 | 6776 | 0.31 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 1.1 | Abengoa Solar, EON | Spain | Abengoa, Eon | Abengoa Solar, EON |  | Abener, Teyma | Spain |  |  | Thermal Oil | Thermal oil/organics | Siemens | Germany | SST-700 | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany |  |  | 12960 | 293 | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) |  |  |  | 300000 | 1 | [6 empty] | 150 | 90 | 12 | 360 | 4 | 600 | 60
Helios I |  | 57 | Spain | Europe | Operational | 50 | 97 |  | 22.15% | Parabolic Trough |  |  |  | 2010 | 2012 | Castilla-La Mancha | Ciudad Real | Puerto Lápice | 39.24,-3.47 | 2092 | 215 | EUR | 2012 | 303.51 | 6070.2 | 0.27 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2010 | EIB €30.6 million | 2.6 | Hyperion | Spain | Hypesol Energy Holding, Hyperion, others |  | REE | Abener, Teyma | Spain |  |  | Thermal Oil | Thermal oil/organics | Siemens | Germany |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany |  |  | 12960 | 293 | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) |  |  |  | 300000 | 1 | [6 empty] | 150 | 90 | 12 | 360 | 4 | 600 | 40
Helios II |  | 58 | Spain | Europe | Operational | 50 | 97 |  | 22.15% | Parabolic Trough |  |  |  | 2010 | 2012 | Castilla-La Mancha | Ciudad Real | Puerto Lápice | 39.24,-3.47 | 2092 | 215 | EUR | 2012 | 303.51 | 6070.2 | 0.27 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2011 | EIB €30.6 million | 2.6 | Hyperion | Spain | Hypesol Energy Holding, Hyperion, others |  | REE | Abener, Teyma | Spain | Radco Industries | USA | Biphenyl/Diphenyl oxide: Xceltherm | Thermal oil/organics | Siemens | Germany |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany |  |  | 12960 | 293 | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) |  |  |  | 300000 | 1 | [6 empty] | 150 | 360 | 12 | 360 | 4 | 600 | 40
La Africana |  | 59 | Spain | Europe | Operational | 50 | 170 |  | 38.81% | Parabolic Trough |  |  |  |  | 2012 | Andalusia | Córdoba | Posadas | 37.755,-5.057 | 2062 | 387 | EUR | 2012 | 546.32 | 10926.4 | 0.28 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 2.5 | Ortiz, TSK, Magtel | Spain | Ortiz, TSK, Magtel |  | Endesa | Sener | Spain | Dow | USA | Biphenyl/Diphenyl oxide:Dowtherm A https://www.diariodesevilla.es/economia/Dow-augura-ralentizacion-termosolar-Espana_0_541446341.html Synthetic Oil http://www.africanaenergia.es/index.php/en/africana-energia.html | Thermal oil/organics | Siemens | Germany | SST-700 | Steam Rankine |  |  |  |  | Wet | 2-tank indirect | 7.5 | 60% Sodium Nitrate, 40% Potassium Nitrate. |  |  | Schott | Germany |  |  |  | 293 | 393 | Sener | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 550000 | 1.8333 | [6 empty] | 150 | 168 | 12 | 672 | 4 | 300 | 40
Liddell Power Station |  | 60 | Australia | Australia | Currently Non-Operational | 3 | 13.55 |  | 51.56% | Linear Fresnel |  |  |  | 2011 | 2012 | New South Wales |  | Liddell | -32.376,150.98 | [14 empty] | $9.25 million from the NSW Government Climate Change Fund Renewable Energy Development Program |  | Novatec Solar | Spain | Macquarie Generation | Macquarie Generation | Australian National Electricity Market | Novatec Solar |  |  |  | Water | Water |  |  |  |  | 55 |  |  |  | Dry | [5 empty] | Novatec | Spain | Nova-1 |  |  | 140 | 270 | [5 empty] | Novatec Solar | Spain |  | 18490 | 1.0272 |  |  |  | 4 | 403
Morón |  | 61 | Spain | Europe | Operational | 50 | 100 |  | 22.83% | Parabolic Trough |  |  |  |  | 2012 | Andalusia | Sevilla | Morón de la Frontera | 37.14,-5.471 | 2068 | 295 | EUR | 2012 | 416.44 | 8328.9 | 0.36 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 1.6 | Ibereolica | Spain | Ibereolica Solar |  | Endesa | Acciona, Seridom | Spain |  |  | Thermal Oil | Thermal oil/organics | Siemens | Germany |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Solel | Israel | UVAC-2008 |  |  | 293 | 393 |  |  | Flagsol, SBP | Germany | SKAL ET-150 | Saint Gobain | France |  | 380000 | 1.2667 | [7 empty] | 116 |  | 464 | 4 | 600 | 45
National Solar Thermal Power Facility |  | 62 | India | Asia | Operational | 1 |  |  |  | Parabolic Trough |  |  |  | 2011 | 2012 |  |  | Gurgaon | 28.428,77.159 | [16 empty] | IIT Bombay | India | IIT Bombay | IIT Bombay | National grid | Abengoa | Spain | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics |  |  |  | Steam Rankine | [10 empty] | Schott | Germany | PTR 70 |  | 360 | 293 | 393 | Shrijee Structures | India |  |  |  | Rioglass | Spain |  | 8000 | 1.3333 | [6 empty] | 120 | 3 | 10 | 12 | 4
Olivenza 1 |  | 63 | Spain | Europe | Operational | 50 | 100 |  | 22.83% | Parabolic Trough |  |  |  | 2010 | 2012 | Extremadura | Badajoz | Olivenza | 38.81,-7.059 | 2053 | 284 | EUR | 2012 | 400.92 | 8018.3 | 0.34 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 1.6 | Ibereolica | Spain | Ibereolica |  | Endesa | Acciona, Seridom | Spain |  |  | Thermal Oil | Thermal oil/organics | Siemens | Germany |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Siemens | Germany | UVAC-2010 |  | 17712 | 293 | 393 | Siemens | Germany | Solel | Israel | SunField 6 | Saint Gobain | France |  | 402210 | 1.3407 | [5 empty] | 545 | 96 | 123 |  | 738 | 6 | 600 | 45
Orellana |  | 64 | Spain | Europe | Operational | 50 | 118 |  | 26.94% | Parabolic Trough |  |  |  |  | 2012 | Extremadura | Badajoz | Orellana | 38.992,-5.549 | 2074 | 240 | EUR | 2012 | 338.8 | 6776 | 0.25 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 1.9 | Acciona | Spain | Acciona |  |  | Sener | Spain |  |  | Thermal Oil | Thermal oil/organics | Siemens | Germany | SST-700 i | Steam Rankine |  |  |  |  | Wet | [5 empty] | Schott | Germany |  |  |  | 293 | 393 |  |  | Sener | Spain | SenerTrough | Rioglass | Spain |  | 405500 | 1.3517 | [7 empty] | 124 |  | 416
Puerto Errado 2 Thermosolar Power Plant |  | 65 | Spain | Europe | Operational | 30 | 49 |  | 18.65% | Linear Fresnel |  |  |  | 2011 | 2012 | Región de Murcia | Murcia | Calasparra | 38.278,-1.6 | 1996 | 120 | EUR | 2012 | 169.4 | 5646.7 | 0.3 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | b1.2 R.D 661/2007 |  | 0.7 | Novatec Biosol | Spain, Germany | Elektra Baselland, Industrielle Werke basel, Novatec Biosol |  | Iberdrola S.A.U., REE | Novatec | Spain |  |  | Water/Steam | Water | GE | USA | Thermodyne |  | 55 |  |  |  | Dry | Single-tank thermocline | 0.5 | Ruths tank |  |  | Novatec | Spain | Nova-1 |  |  | 140 | 270 |  |  | Novatec | Germany |  | Novatec Solar España S.L. | Spain |  | 302000 | 1.6778 |  |  | 16 | 28 | 940 | [7 empty] | 25
Solaben 2 |  | 66 | Spain | Europe | Operational | 50 | 100 |  | 22.83% | Parabolic Trough |  |  |  |  | 2012 | Extremadura | Cáceres | Logrosán | 39.225,-5.391 | 2076 | 229 | EUR | 2012 | 323.27 | 6465.5 | 0.28 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 1.1 | Abengoa | Spain | Abengoa (70%), Itochu (30%) | Abengoa |  | Abener, Teyma | Spain |  |  | Thermal Oil | Thermal oil/organics |  |  |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany |  |  | 12960 | 293 | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) |  |  |  | 300000 | 1 | [6 empty] | 150 | 90 | 12 | 360 | 4 | 700 | 85
Solaben 3 |  | 67 | Spain | Europe | Operational | 50 | 100 |  | 22.83% | Parabolic Trough |  |  |  |  | 2012 | Extremadura | Cáceres | Logrosán | 39.225,-5.391 | 2076 | 229 | EUR | 2012 | 323.27 | 6465.5 | 0.28 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 1.1 | Abengoa | Spain | Abengoa (70%), Itochu (30%) | Abengoa |  | Abener, Teyma | Spain |  |  | Thermal Oil | Thermal oil/organics |  |  |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany |  |  | 12960 | 293 | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) |  |  |  | 300000 | 1 | [6 empty] | 150 | 90 | 12 | 360 | 4 | 700 | 85
Solacor 1 |  | 68 | Spain | Europe | Operational | 50 | 100 |  | 22.83% | Parabolic Trough |  |  |  |  | 2012 | Andalusia | Córdoba | El Carpio | 37.957,-4.492 | 2042 | 229 | EUR | 2012 | 323.27 | 6465.5 | 0.28 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 1.1 | Abengoa | Spain | Abengoa (76%), JGC (24%() | Abengoa |  | Abener, Teyma | Spain |  |  | Thermal Oil | Thermal oil/organics |  |  |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany |  |  | 12960 | 293 | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) |  |  |  | 300000 | 1 | [6 empty] | 150 | 90 | 12 | 360 | 4 | 450 | 40
Solacor 2 |  | 69 | Spain | Europe | Operational | 50 | 100 |  | 22.83% | Parabolic Trough |  |  |  |  | 2012 | Andalusia | Córdoba | El Carpio | 37.957,-4.492 | 2042 | 229 | EUR | 2012 | 323.27 | 6465.5 | 0.28 | 0.27 | EUR | 2012 | 0.38 | 25 | FIT | Real Decreto 661/2007 |  | 1.1 | Abengoa | Spain | Abengoa (76%), JGC (24%() | Abengoa |  | Abener, Teyma | Spain |  |  | Thermal Oil | Thermal oil/organics |  |  |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany |  |  | 12960 | 293 | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) |  |  |  | 300000 | 1 | [6 empty] | 150 | 90 | 12 | 360 | 4 | 450 | 40
Thai Solar Energy 1 |  | 70 | Thailand | Asia | Operational | 5 | 8 |  | 18.26% | Parabolic Trough |  |  |  |  | 2012 | Kanchanaburi Province |  | Huai Kachao | 14.334,99.709 | [7 empty] | 11.5 | THB | 2012 | 0.42 | 10 |  | Feed-in Tariff |  | 1.1 | Solarlite | Germany | Thai Solar Energy Co.Ltd. | Thai Solar Energy Co.Ltd. | Electricity Generating Authority of Thailand | Solarlite GmbH |  |  |  | Water | Water | MAN Turbo | Germany | 2-Mar |  | 30 | [9 empty] | Schott | Germany |  |  |  | 201 | 340 |  |  | Solarlite GmbH | Germany | SL 4600 | Guardian & AGC | France |  | 45000 | 1.5 | [6 empty] | 120 | 19 | 10 | 86 |  | 120 | 10
Arenales |  | 71 | Spain | Europe | Operational | 50 | 166 |  | 37.9% | Parabolic Trough |  |  |  | 2011 | 2013 | Andalusia | Sevilla | Morón de la Frontera | 37.162,-5.548 | 2064 | 313.5 | EUR | 2013 | 450.01 | 9000.3 | 0.23 | 0.27 | EUR | 2013 | 0.39 | 25 | FIT | Real Decreto 661/2007 |  | 2.2 | Solar millennium, OHL, Deutsche Bank | Germany | RREF, OHL | OHL |  | Ecolair España | Spain | Lanxess | Germany | Biphenyl/Diphenyl oxide: Diphyl | Thermal oil/organics | GE | USA |  | Steam Rankine |  |  |  |  | Wet | 2-tank indirect | 7 | Molten salts; 60% Sodium Nitrate, 40% Potassium Nitrate. |  |  | Siemens | Germany | UVAC-2010 |  | 22464 | 293 | 393 | Siemens | Germany | Solel | Israel | SunField 6 |  |  |  | 510120 | 1.7004 | [5 empty] | 545 | 96 | 156 |  | 936 | 6
ASE Demo Plant |  | 72 | Italy | Europe | Operational | 0.4 | 0.28 |  | 7.991% | Parabolic Trough |  |  |  |  | 2013 | Umbria |  | Massa Martana | 42.73,12.529 | 1527 | [14 empty] | 0.03 | Archimede Solar Energy | Italy | Archimede Solar Energy |  |  | Chiyoda Corporation | Japan |  |  | Molten salt | Salt | Siemens | Germany |  | Steam Rankine |  | 15.6 |  |  |  | 2-tank direct | 4.27 | Molten salt | [7 empty] | 290 | 550 | [8 empty] | 3398 | 1.4158 | [7 empty] | 1 |  | 6
Casablanca |  | 73 | Spain | Europe | Operational | 50 | 160 |  | 36.53% | Parabolic Trough |  |  |  |  | 2013 | Extremadura | Badajoz | Talarrubias | 39.239,-5.314 | 2064 | 345 | EUR | 2013 | 495.23 | 9904.6 | 0.27 | 0.27 | EUR | 2013 | 0.39 | 25 | FIT | Real Decreto 661/2007 | EIB €140 million | 2 | Cobra | Spain | ACS/Cobra |  | Endesa | Cobra | Spain |  |  | Biphenyl/Diphenyl oxide | Thermal oil/organics | Siemens | Germany |  | Steam Rankine | 100 | 38.1 |  |  | Wet | 2-tank indirect | 7.5 | 60% Sodium Nitrate, 40% Potassium Nitrate. |  |  | Solel | Israel | UVAC-2008 |  | 22464 | 293 | 393 | Sener | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 510120 | 1.7004 | [5 empty] | 817 | 144 | 156 | 12 | 624 | 4
Enerstar |  | 74 | Spain | Europe | Operational | 50 | 100 |  | 22.83% | Parabolic Trough |  |  |  | 2010 | 2013 | Comunidad Valenciana | Alicante | Villena | 38.729,-0.922 | 1992 | 225 | EUR | 2013 | 322.98 | 6459.5 | 0.28 | 0.27 | EUR | 2013 | 0.39 | 25 | FIT | Real Decreto 661/2007 |  | 2.1 | FCC Energy | Spain | FCC Energy |  |  | FCC, IDOM | Spain |  |  | Thermal Oil | Thermal oil/organics | MAN Turbo | Germany |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany | PTR 70 |  |  | 293 | 393 | Sener | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 339506 | 1.1317 | [6 empty] | 150 | 105 | 12 | 420 | 4
Godawari Solar Project |  | 75 | India | Asia | Operational | 50 | 118 |  | 26.94% | Parabolic Trough |  |  |  | 2011 | 2013 | Rajhastan |  | Nokh | 27.601,72.224 | 1667 | 7900 | INR | 2013 | 145.71 | 2914.1 | 0.11 | 12.2 | INR | 2013 | 0.23 | 25 | PPA |  |  | 1.5 | Godawari Green Energy | India | Godawari Green Energy |  | NTPC Vidyut Vyapar Nigam Limited | Lauren Engineering | USA | Dow | USA | Biphenyl/Diphenyl oxide: Dowtherm A | Thermal oil/organics | Siemens | Germany | SST-700 | [5 empty] | Wet | [5 empty] | Schott | Germany | PTR 70 |  |  | 293 | 390 |  |  | SBP, Flagsol | Germany | SKAL ET-150 | Flabeg | Germany | RP3 | 392400 | 1.308 | [5 empty] | 817 | 144 | 120 | 12 | 480 | 4
KVK Energy Solar Project |  | 76 | India | Asia | Currently Non-Operational | 100 |  |  |  | Parabolic Trough |  |  |  |  | 2013 | Rajasthan |  | Askandra | 27.382,71.773 | 1940 |  |  | 2017 |  |  |  | 11.2 | INR | 2017 | 0.18 |  | PPA |  |  |  | KVK Energy Ventures Ltd | India | KVK Energy Ventures Ltd, Lanco |  | NTPC Vidyut Vyapar Nigam Limited | Initec, Lanco | Spain, India |  |  | Synthetic Oil | Thermal oil/organics | Siemens | Germany | SST-700 | [5 empty] | Wet | 2-tank indirect | 4 | 1010 MWht, Molten Salt | [9 empty] | Sener | Spain | Sener | Spain | SNT0/ SenerTROUGH | [12 empty] | 290
Shams 1 |  | 77 | United Arab Emirates | MENA | Operational | 100 | 210 |  | 23.97% | Parabolic Trough |  |  | Natural gas boiler | 2010 | 2013 | Abu Dhabi |  | Madinat Zayed | 23.57,53.716 | 2019 | 600 | USD | 2013 | 648.32 | 6483.2 | 0.27 |  |  | 2013 |  | 25 | PPA | Private PPA |  | 2.5 | Masdar, Total, Abengoa | UAE, France, Spain | Masdar 60%, Total 20%, (Abengoa 20% later sold to Madar) |  | ADWEC | Abener, Teyma | Spain | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics | MAN Turbo | Germany |  | Steam Rankine |  |  |  |  | Dry | [5 empty] | Schott | Germany | PTR 70 |  | 27648 | 300 | 400 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) | Flabeg | Germany | RP3 | 627840 | 1.0464 | [6 empty] | 150 | 192 | 12 | 768 | 4
Solaben 1 |  | 78 | Spain | Europe | Operational | 50 | 100 |  | 22.83% | Parabolic Trough |  |  |  |  | 2013 | Extremadura | Cáceres | Logrosán | 39.225,-5.391 | 2076 | 240 | EUR | 2013 | 344.51 | 6890.2 | 0.3 | 0.27 | EUR | 2013 | 0.39 | 25 | FIT | Real Decreto 661/2007 | EIB €100 million (200 million for Solaben 1 and 6) | 1.1 | Abengoa | Spain | Abengoa | Abengoa |  | Abener, Teyma | Spain |  |  | Thermal Oil | Thermal oil/organics |  |  |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany |  |  | 12960 | 293 | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) |  |  |  | 300000 | 1 | [6 empty] | 150 | 90 | 12 | 360 | 4 | 700 | 85
Solaben 6 |  | 79 | Spain | Europe | Operational | 50 | 100 |  | 22.83% | Parabolic Trough |  |  |  |  | 2013 | Extremadura | Cáceres | Logrosán | 39.225,-5.391 | 2076 | 229 | EUR | 2013 | 328.72 | 6574.4 | 0.28 | 0.27 | EUR | 2013 | 0.39 | 25 | FIT | Real Decreto 661/2007 | EIB €100 million (200 million for Solaben 1 and 6) | 1.1 | Abengoa | Spain | Abengoa | Abengoa |  | Abener, Teyma | Spain |  |  | Thermal Oil | Thermal oil/organics |  |  |  | Steam Rankine | 100 |  |  |  | Wet | [5 empty] | Schott | Germany |  |  | 12960 | 293 | 393 | Abengoa | Spain | Abengoa | Spain | Astro (ET-150) |  |  |  | 300000 | 1 | [6 empty] | 150 | 90 | 12 | 360 | 4 | 700 | 85
Solana Generating Station |  | 80 | United States | North America | Operational | 250 | 944 |  | 43.11% | Parabolic Trough |  |  | Natural gas boiler | 2010 | 2013 | Arizona | Gila Bend | Phoenix | 32.917,-112.967 | 2784 | 2000 | USD | 2013 | 2161.06 | 8644.3 | 0.2 | 0.14 | USD | 2013 | 0.15 | 30 | PPA |  | Federal Loan Guarantee $1.45 billion, 30% investment tax credit | 7.8 | Abengoa | Spain | Abengoa |  | Arizona Public Service | Abener, Teyma | Spain | Eastman; Radco | USA | Biphenyl/Diphenyl oxide: Xceltherm | Thermal oil/organics |  |  |  | Steam Rankine | 100 |  |  |  | Wet | 2-tank indirect | 6 | Molten salts |  |  | Schott | Germany |  |  |  | 293 | 393 | Abengoa | Spain | Abengoa | Spain | E2 | Rioglass | Spain |  | 2200000 | 1.4667 | [7 empty] | 808 | 10 | 3232 | 4 | 1500 | 85
SUPCON Delingha 10 MW Tower | 中控太阳能德令哈10兆瓦塔式熔盐储能光热电站 | 81 | China | Asia | Operational | 10 | 24 |  | 27.4% | Power Tower |  |  |  | 2010 | 2013 | Qinghai | Haixi | Delingha | 37.366,97.293 | 2043 | 150 | RMB | 2013 | 26.35 | 2634.9 | 0.09 | 1.24 | RMB | 2013 | 0.21 | 20 | FIT |  |  |  | SUPCON Solar | China | SUPCON Solar |  | Qinghai State Grid Electric Power | SUPCON solar | China | Zhejiang Lianda Chemical Company (supply of Sodium nitrate) | China | Water | Water | Hangzhou Steam Turbine Company | China | N10-8.83/510 | Steam Rankine | 88.3 | 0.314 | Hangzhou Boiler Group | China | Wet | 2-tank direct | 2 | Molten salt | Bluestar (Beijing) Chemical Machinery Co., Ltd. | China | Hangzhou Boiler Group | China | External - cylindrical | 80 |  | 310 | 565 | Supcon | China | Supcon | China | SUPCON | Taiwan Glass Yueda Solar Mirror Co., Ltd | China |  | 63000 | 1.05 | 22500 | 2 | [10 empty] | 100 | http://www.cspfocus.cn/study/pdetail_208.htm?from=singlemessage&isappinstalled=0
Termosol 1 |  | 82 | Spain | Europe | Operational | 50 | 180 |  | 41.1% | Parabolic Trough |  |  |  | 2011 | 2013 | Extremadura | Badajoz | Navalvillar de Pela | 39.193,-5.576 | 2077 | 409.5 | EUR | 2013 | 587.82 | 11756.3 | 0.28 | 0.27 | EUR | 2013 | 0.39 | 25 | FIT | Real Decreto 661/2007 |  | 2 | NextEra, Florida Power & Light | USA | NextEra, FPL |  |  | Sener | Spain |  |  | Thermal Oil | Thermal oil/organics |  |  |  | Steam Rankine |  |  |  |  | Wet | 2-tank indirect | 9 | 60% Sodium Nitrate, 40% Potassium Nitrate. | [7 empty] | 293 | 393 | Sener | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 523200 | 1.744 | [5 empty] | 817 |  | 160 |  | 640 | 4
Termosol 2 |  | 83 | Spain | Europe | Operational | 50 | 180 |  | 41.1% | Parabolic Trough |  |  |  | 2011 | 2013 | Extremadura | Badajoz | Navalvillar de Pela | 39.193,-5.576 | 2077 | 409.5 | EUR | 2013 | 587.82 | 11756.3 | 0.28 | 0.27 | EUR | 2013 | 0.39 | 25 | FIT | Real Decreto 661/2007 |  | 2 | NextEra, Florida Power & Light | USA | NextEra, FPL |  |  | Sener | Spain |  |  | Thermal Oil | Thermal oil/organics |  |  |  | Steam Rankine |  |  |  |  | Wet | 2-tank indirect | 9 | 60% Sodium Nitrate, 40% Potassium Nitrate. | [7 empty] | 293 | 393 | Sener | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 523200 | 1.744 | [5 empty] | 817 |  | 160 |  | 640 | 4
Airlight Energy Ait-Baha Pilot Plant |  | 84 | Morocco | MENA | Operational | 3 | 2.39 |  | 9.094% | Parabolic Trough |  |  |  | 2012 | 2014 | Souss-Massa |  | Ait Baha | 30.218,-9.149 | 2200 | [14 empty] | 0.24 | Airlight Energy | Switzerland | Cimar, Italcementi Group | Cimar, Italcementi Group | Cimar, Italcementi Group |  |  |  |  | Air | Air | Turboden | Italy |  | Organic Rankine | [5 empty] | Other | 5 | Packed-bed of rocks |  |  | Ailight Energy |  |  |  | 108 | 270 | 570 | [5 empty] | Airlight Energy | Switzerland |  | 6159 | 0.34217 | [5 empty] | 2053 | 215 | 1 | 12 | 3 | 3
City of Medicine Hat ISCC Project |  | 85 | Canada | North America | Operational | 1.1 | 1.5 |  | 15.57% | ISCC; Trough | 203 | 184.5455 | ISCC | 2013 | 2014 |  |  | Medicine Hat | 50.04,-110.72 |  | 9 | USD | 2014 | 9.93 | 9024.3 | 0.57 | [9 empty] | City of Medicine Hat | USA | City of Medicine Hat |  |  |  |  | Radco Industries | USA | Biphenyl/Diphenyl oxide: Xceltherm | Thermal oil/organics | [23 empty] | SkyFuel | USA | SkyTrough |  |  |  | 5248 | 0.79515 | [5 empty] | 656 | 115 | 2 |  | 8 | 4
Dhursar |  | 86 | India | Asia | Operational | 125 | 280 |  | 25.57% | Linear Fresnel |  |  |  |  | 2014 | Rajasthan |  | Dhursar | 26.786,72.008 | 1742 | 21000 | INR | 2014 | 366.24 | 2929.9 | 0.11 | 11.97 | INR | 2014 | 0.21 | 25 | PPA |  | Asian Development Bank $103 million; also from FMO (Dutch development bank) | 3.4 | Rajasthjan Sun Technique Energy, Areva | India, France | Reliance power |  | NTPC Vidyut Vyapar Nigam | Areva | France |  |  | Water/Steam http://oa.upm.es/23011/1/INVE_MEM_2013_151623.pdf | Water |  |  |  | Steam Rankine |  |  |  |  | Wet | [14 empty] | Areva Solar | USA | [9 empty] | 0
Genesis Solar Energy Project |  | 87 | United States | North America | Operational | 250 | 580 |  | 26.48% | Parabolic Trough |  |  |  | 2010 | 2014 | California |  | Blythe | 33.667,-114.983 | 2676 | 1215.5 | USD | 2014 | 1292.79 | 5171.2 | 0.19 | 0.16 | USD | 2014 | 0.17 | 25 | PPA |  | Federal Loan Guarantee $852 million, 30% investment tax credit | 7.9 | NextEra, Genesis Solar | USA | Genesis Solar | Genesis Solar, LLC | Pacific Gas & Electric (PG&E) | Blattner Energy | USA | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics |  |  |  | Steam Rankine |  |  |  |  | Dry | [5 empty] | ARB Inc | USA |  |  |  |  | 393 | Sener | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 1928320 | 1.2855 | [7 empty] | 460 |  | 1840 | 4 | 1085 | 50
Ivanpah Solar Electric Generating System |  | 88 | United States | North America | Operational | 377 | 1079 |  | 32.67% | Power Tower |  |  | Natural gas boiler | 2010 | 2014 | California |  | Primm, NV | 35.552,-115.459 | 2768 | 2200 | USD | 2014 | 2339.89 | 6206.6 | 0.19 | 0.14 | USD | 2014 | 0.14 | 25 | PPA |  | Federal Loan Guarantee $1.6 billion, 30% investment tax credit | 14.2 | BrightSource | USA | NRG, Brightsource, Google |  | Pacific Gas & Electric; Southern California Edison | Bechtel Engineering | USA |  |  | Water | Water | Siemens | Germany | SST-900 | Steam Rankine | 160 |  |  |  | Dry | [5 empty] | Riley | USA | Solar receiver steam generator | 140 |  |  |  | Brightsource | USA | Brightsource | USA | Brightsource | Guardian | USA | EcoGuard Solar Boost | 2600000 | 1.1494 | 173500 | 15 | [9 empty] | 1896 | 90
Megha Solar Plant |  | 89 | India | Asia | Operational | 50 | 110 |  | 25.11% | Parabolic Trough |  |  |  | 2011 | 2014 | Andhra Pradesh |  | Anantapur | 14.949,77.688 | 1476 | 8480 | INR | 2014 | 147.89 | 2957.8 | 0.12 | 11.31 | INR | 2014 | 0.2 | 25 | PPA |  | loan from KfW €250m for 125MW project of which the Megha station is a part | 2.42 | Megha Engineering and Infrastructure | India | Megha Engineering and Infrastructure |  | NTPC Vidyut Vyapar Nigam Ltd. | MEIL Green Power | India | Radco Industries | USA | Biphenyl/Diphenyl oxide:Xceltherm-MK1 | Thermal oil/organics | GE | USA |  | Steam Rankine |  |  |  |  | Wet | [5 empty] | Siemens | Germany | UVAC-2010 |  | 16128 | 293 | 393 | Albiasa | Spain | Albiasa | Spain | AT-150 |  |  |  | 366240 | 1.2208 | [5 empty] | 817 | 150 | 112 | 12 | 448 | 4
Mojave Solar Project |  | 90 | United States | North America | Operational | 280 | 600 |  | 24.46% | Parabolic Trough |  |  |  | 2011 | 2014 | California |  | Harper Dry Lake | 35.017,-117.333 | 2888 | 1600 | USD | 2014 | 1701.74 | 6077.6 | 0.24 | 0.15 | USD | 2014 | 0.16 | 25 | PPA |  | Federal Loan Guarantee $1.2 billion, 30% investment tax credit | 7.1 | Abengoa | Spain | Mojave Solar |  | Pacific Gas & Electric (PG&E) | Abener, Teyma | Spain | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics | GE | USA |  | Steam Rankine |  |  |  |  | Wet | [5 empty] | Schott | Germany | PTR 70 |  |  |  |  | Abengoa | Spain | Abengoa | Spain | E2 | Rioglass | Spain |  | 1559347 | 0.92818 | [8 empty] | 10 |  |  | 1200 | 80
Rende-CSP Plant |  | 91 | Italy | Europe | Operational | 1 | 3 |  | 34.25% | Linear Fresnel |  |  |  | 2013 | 2014 | Calabria |  | Rende | 39.374,16.246 | [15 empty] | 0.02 | Falck Renewables | Italy | Falck Renewables |  |  | Elianto |  |  |  | Diathermic oil |  |  |  |  | Organic Rankine | [16 empty] | 280 | [8 empty] | 9780 | 1.63
Crescent Dunes Solar Energy Project |  | 92 | United States | North America | Operational | 110 | 500 |  | 51.89% | Power Tower |  |  |  | 2011 | 2015 | Nevada |  | Tonopah | 38.239,-117.363 | 2734 | 983 | USD | 2015 | 1032.24 | 9384 | 0.18 | 0.14 | USD | 2015 | 0.14 | 25 | Tender/PPA |  | Federal Loan Guarantee $737 million, 30% investment tax credit | 6.5 | SolarReserve, ACS Cobra | USA, Spain | SolarReserve | SolarReserve's Tonopah Solar Energy, LLC | NV Energy | Cobra | Spain |  |  | Molten salt | Salt | Alstom | France |  | Steam Rankine | 115 |  |  |  | Hybrid | 2-tank direct | 10 | Thermal energy storage achieved by raising salt temperature from 550 to 1050 F. Thermal storage efficiency is 99% |  |  | Rocketdyne (SolarReserve) | USA | External - cylindrical | 195 | [5 empty] | Solarrserve | USA | Rocketdyne (Solarreserve) | Flabeg | Germany |  | 1197148 | 1.8139 | 10347 | 116
KaXu Solar One |  | 93 | South Africa | Sub-Saharan Africa | Operational | 100 | 330 |  | 37.67% | Parabolic Trough |  |  |  | 2012 | 2015 | Northern Cape | Namakwa District Municipality | Pofadder | -28.902,19.621 | 2963 | 860 | USD | 2015 | 903.08 | 9030.8 | 0.24 | 2.69 | ZAR | 2015 | 0.22 |  | PPA |  | Development Bank of South Africa $146 million, €220 million EIB; IFC $125 million, mobilization of senior loan from CTF $26.5 million, |  | Abengoa | Spain | Abengoa |  | Eskom | Abener, Teyma | Spain |  |  | Thermal Oil | Thermal oil/organics | Siemens | Germany |  | Steam Rankine | 100 |  |  |  | Dry | 2-tank indirect | 2.5 | Molten salts |  |  | Schott | Germany | PTR 70 |  |  |  |  | Abengoa | Spain | Abengoa | Spain | E2 | Rioglass | Spain |  | 800000 | 1.3333 | [7 empty] | 300 | 10 | 1200 | 4
NOOR I |  | 94 | Morocco | MENA | Operational | 160 | 370 |  | 26.4% | Parabolic Trough | 70 | 0.4375 | LFO Boiler System; Co-located PV; no economic hybridisation | 2013 | 2015 | Drâa-Tafilalet |  | Ouarzazate | 30.994,-6.863 | 2497 | 1042 | EUR | 2015 | 1214.26 | 7589.1 | 0.28 | 1.62 | MAD | 2015 | 0.18 | 25 | PPA |  | Loans: €168 million African Development Bank (AfDB); €70 million Clean Technology Fund (CTF)/AfDB; €140 million World Bank; €68 million CTF/World Bank; €100 million EIB; €100 million AFD; €100 million KfW. Grants: €30 million NIF; €266 million MASEN |  | ACWA | Saudi Arabia | ACWA |  | ONE and MASEN | Acciona, Sener, TSK | Spain | Dow | USA | Biphenyl/Diphenyl oxide: Dowtherm A | Thermal oil/organics | Siemens | Germany | SST- 700/900 | Steam Rankine |  |  |  |  | Wet | 2-tank indirect | 3 | Molten Salt |  |  | Schott | Germany | PTR 70 |  |  | 293 | 393 | Sener | Spain | Sener | Spain | SenerTrough | Flabeg | Germany | RP3 | 1308000 | 1.3625
Stillwater GeoSolar Hybrid Plant |  | 95 | United States | North America | Operational | 2 | 3 |  | 17.12% | Parabolic Trough |  |  |  | 2014 | 2015 | Nevada |  | Fallon | 39.548,-118.556 | [11 empty] | 20 |  |  |  | 0.08 | ENEL | Italy | ENEL | Enel | NV Energy | SkyFuel |  |  |  | Water | Water |  |  |  | Organic Rankine | [19 empty] | SkyFuel | USA | SkyTrough | ReflecTech | USA | [8 empty] | 656 | 115 |  | 8
Aalborg CSP-Brønderslev CSP with ORC project |  | 96 | Denmark | Europe | Operational | 5.5 |  |  |  | Biomass-Hybrid; Trough |  |  | Biomass-organic rankine cycle (ORC) for Combined Heat and Power | 2016 | 2016 | North Jutland |  | Brønderslev | 57.254,9.989 | 1025 |  |  | 2016 | [5 empty] | 2016 |  |  |  |  | Danish Government’s Energy Technology Development and Demonstration Programme (EUDP) |  | Aalborg CSP | Denmark | Brønderslev Forsynin |  |  | Aalborg CSP | Denmark | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics |  |  |  | Organic Rankine | [10 empty] | Aalborg CSP | Denmark |  |  | 1200 | 252 | 312 | Aaltrough | Denmark | Aalborg CSP | Denmark | Aaltrough |  |  |  | 26929 | 0.81603 | [5 empty] | 674 | 125 | 10 | 10 | 40 | 4
Bokpoort |  | 97 | South Africa | Sub-Saharan Africa | Operational | 50 | 230 |  | 52.51% | Parabolic Trough | 10 | 0.2 | LFO Boiler System (2x5 MWht) | 2013 | 2016 | Northern Cape | ZF Mgcawu District Municipality | Groblershoop | -28.74,21.995 | 2949 | 565 | USD | 2016 | 585.83 | 11716.6 | 0.22 | 2.52 | ZAR | 2016 | 0.18 | 20 | PPA |  |  | 1 | ACWA | Saudi Arabia | ACWA |  | Eskom | Sener, Acciona, TSK | Spain | Dow | USA | Biphenyl/Diphenyl oxide: Dowtherm A | Thermal oil/organics | Siemens | Germany | SST 800 | Steam Rankine |  |  |  |  | Wet | 2-tank indirect | 9.3 | Molten salts (1300 MWht) |  |  | Schott | Germany | PTR 70 |  | 26000 | 293 | 393 | Sener | Spain | Sener | Spain | SenerTrough | Flabeg FE | Germany | RP3 | 588600 | 1.962 | [7 empty] | 180
Lanzhou Dacheng Dunhuang (DCTC Dunhuang) - 10MW Fresnel | 敦煌10兆瓦线性菲涅尔式聚光太阳能光热连续发电项目 | 98 | China | Asia | Operational | 10 | 60 |  | 68.49% | Linear Fresnel |  |  |  |  | 2016 | Gansu | Jiuquan | Dunhuang | 40.084,94.421 | 1786 | [14 empty] | 0.6 | Dunhuang Dacheng Concentrating Thermal Power Co. (Lanzhou Dacheng Technology Co., Ltd) | China | Dunhuang Dacheng Concentrating Thermal Power Co. (Lanzhou Dacheng Technology Co., Ltd) |  | State Grid Gansu Electric Power Company | Lanzhou Dacheng Concentrating Energy Technology (Lanzhou Dacheng Technology Co., Ltd) |  |  |  | Molten salt | Salt |  |  |  | Steam Rankine | [6 empty] | 16 | Molten Salt |  |  | Lanzhou Dacheng Vacuum Technology Co. (Lanzhou Dacheng Technology Co., Ltd) | China | [28 empty] | http://www.lzdctc.com/w/hdcontentdisp-7-904-201558-305235.htm; http://www.cspplaza.com/article-7371-1.html
Khi Solar One |  | 99 | South Africa | Sub-Saharan Africa | Operational | 50 | 180 |  | 41.1% | Power Tower |  |  |  | 2012 | 2016 | Northern Cape | ZF Mgcawu District Municipality | Upington | -28.537,21.078 | 2952 | 450 | USD | 2016 | 466.59 | 9331.8 | 0.22 | 2.69 | ZAR | 2016 | 0.19 | 20 | PPA |  | European Investment Bank (EIB) €50 million; CTF $15 million; IFC app. $75 million;C Loan $15 million |  | Abengoa | Spain | Abengoa | Abengoa Solar | Eskom | Abener, Teyma | Spain |  |  | Water/Steam | Water |  |  |  | Steam Rankine |  |  |  |  | Dry | Other | 2 | Saturated steam |  |  | Cockerill | Belgium |  | 200 |  |  |  | Abengoa | Spain | Abengoa | Spain | ASUP 140 |  |  |  | 576800 | 1.9227 | 4120 | 140
Shouhang Dunhuang Phase I - 10 MW Tower | 北京首航节能新能源有限公司敦煌10兆瓦熔盐塔式光热发电项目 | 100 | China | Asia | Operational | 10 |  |  |  | Power Tower |  |  |  | 2014 | 2016 | Gansu | Jiuquan | Dunhuang | 40.083,94.434 | 1777 | 420 | RMB | 2016 | 65.58 | 6557.8 |  | 0.3 | RMB | 2016 | 0.18 | 20 |  |  | Asian Development Bank $100 million | 1.2 | Shouhang | China | Shouhang |  | Gansu State Grid Electric Power | Suncan (Shouhang) | China |  |  | Molten salt | Salt |  |  |  | Steam Rankine | [5 empty] | 2-tank direct | 15 | Molten salt |  |  | Shouhang | China | External - cylindrical | 138 |  |  |  | Shouhang | China | Shouhang | China |  |  |  |  | 175375 | 2.9229 | 1525 | 116 | [11 empty] | https://www.sohu.com/a/312422783_734062
Sundrop CSP Project |  | 101 | Australia | Australia | Operational | 1.5 | 1.7 |  | 12.94% | Power Tower |  |  |  | 2015 | 2016 | South Australia |  | Port Augusta | -32.594,137.856 | [16 empty] | Aalborg CSP | Denmark | Sundrop Farms |  |  | John Holland |  |  |  | Water | Water |  |  |  | Steam Rankine | [13 empty] | 127 | [5 empty] | eSolar | USA | SCS5 |  |  |  | 51505 | 5.7228 | 23712
Agua Prieta II |  | 102 | Mexico | North America | Operational | 12 | 34 |  | 32.34% | ISCC; Trough | 394 | 32.8333 | ISCC | 2011 | 2017 | Sonora |  | Agua Prieta | 31.326,-109.549 | [14 empty] | Global environmental facility subvention | 0.6 | Abengoa Solar | Spain | Federal Electricity Commission |  |  | Abener | Spain |  |  | Thermal Oil |  |  |  |  | Steam Rankine | [19 empty] | Abgeoa |  | ASTRO | Rioglass | Spain |  | 85000 | 1.1806 | [6 empty] | 150 | 26 |  | 104 | 4
Jemalong Solar Thermal Station |  | 103 | Australia | Australia | Operational | 1.1 | 2.2 |  | 22.83% | Power Tower |  |  |  | 2014 | 2017 | New South Wales |  | Jemalong | -33.4,148.1 |  | 21 | AUD | 2017 | 16.41 | 14919.4 | 0.64 | [7 empty] | AU$8.89 million from ARENA | 0.1 | Vast Solar | Australia | Vast Solar | Vast Solar | Essential Energy |  |  |  |  | Liquid sodium |  |  |  |  | Steam Rankine |  |  |  |  | Dry | 2-tank direct | 3 | Liquid sodium |  |  | Vast Solar |  |  | 30 | [5 empty] | Vast Solar | Australia |  |  |  |  | 15000 | 2.2727 | 3500
CGN Delingha - 50MW Trough | 中广核太阳能德令哈有限公司导热油槽式5万千瓦光热发电项目 | 104 | China | Asia | Operational | 50 | 199 |  | 45.43% | Parabolic Trough |  |  |  | 2014 | 2018 | Qinghai | Haixi | Delingha | 37.356,97.271 | 1950 | 1938 | RMB | 2018 | 292.07 | 5841.4 | 0.13 | 1.15 | RMB | 2018 | 0.17 | 20 | FIT | Chinese Demonstration Program 1st Batch | Asian development bank 150 million USD; The export-import bank of China 78.58 million USD |  | CGN Delingha Solar Energy | China | CGN Deligha Solar Energy |  |  | Suncan (Shouhang) | China | Eastman/Solutia | USA | Biphenyl/Diphenyl oxide: Therminol VP-1 | Thermal oil/organics | Dongfang Boilor | China |  | Steam Rankine | 100 | 40 | Harbin Turbine Company; WCE-Wuxi Chemical | China | Wet | 2-tank indirect | 9 | Molten salt | IDOM | Spain | Rioglass | Spain | PTR70 |  | 27360 | 293 | 393 | TSK-Ingeteam | Spain | SBP | Germany | ET-150 | Rioglass | Spain | RP3 | 620000 | 2.0667 | 150 |  |  |  |  | 620000 | 150 | 190 | 12 | 760 | 4 | 1300 | 100 | https://www.nengapp.com/news/detail/1914584
Huaqiang TeraSolar 15MW Fresnel | 华强兆阳张家口一号15MW光热示范电站 | 105 | China | Asia | Operational | 15 | 75 |  | 57.08% | Linear Fresnel | 50 | 3.3333 | Retrofitted with 50 MW PV in 2023 | 2015 | 2018 | Hebei | Zhangjiakou | Zhangbei | 41.214,114.573 |  | 700 | RMB | 2018 | 105.49 | 7033 | 0.12 |  | RMB | 2018 | [6 empty] | Shenzhen Huaqiang Zhaoyang Energy (Xinli Energy Development Co., Ltd.) | China | Zhangbei Huaqiang Zhaoyang Co., Ltd. (Xinli Energy Development Co., Ltd.) |  |  | TeraSolar, Xian New Energy | China | TeraSolar | China | Water | Water |  |  |  | Steam Rankine | [5 empty] | Other | 14 | Solid state formulated concrete | TeraSolar | China | TeraSolar | China | [7 empty] | TeraSolar | China | HLIACS |  |  |  | 170000 | 1.8889 | [13 empty] | http://en.cspplaza.com/overview-of-huaqiang-terasolar-i-15mw-csp-project-2; https://www.sohu.com/a/156359415_654874; http://helioscsp.com/concentrated-solar-power-technology-dsgconcrete-tes-has-been-commercialized-in-china/; http://cnste.org/html/xiangmu/2021/0702/8076.html
Ilanga I |  | 106 | South Africa | Sub-Saharan Africa | Operational | 100 | 320 |  | 36.53% | Parabolic Trough |  |  |  | 2015 | 2018 | Northern Cape | ZF Mgcawu District Municipality | Upington | -28.49,21.541 | 2937 | 690 | USD | 2015 | 724.57 | 7245.7 | 0.19 | 1.9 | ZAR | 2015 | 0.16 | 20 | PPA |  | Development Bank of Southern Africa 58.8 million USD |  | Emvelo, Cobra | South Africa; Spain | Karoshoek Solar One (RF) Proprietary Limited |  |  | Emvelo, Dankocom (COBRA + SENER) | Spain, South Africa |  |  | Thermal Oil | Thermal oil/organics |  |  |  | Steam Rankine |  |  |  |  | Dry | 2-tank indirect | 4.5 | Molten salt |  |  | Rioglass | Spain |  |  |  | 293 | 393 | Sener | Spain | Sener | Spain | SenerTrough |  |  |  | 869800 | 1.4497 | [7 empty] | 266 |  | 1064 | 4
ISCC Waad Al Shamal |  | 107 | Saudi Arabia | MENA | Operational | 50 |  |  |  | ISCC; Trough | 1390 | 27.8 | ISCC | 2018 | 2018 |  |  | Waad Al Shamal | 31.631,38.874 | 2521 | [15 empty] | General Electric | USA | Saudi Electriciy Company | [6 empty] | Thermal Oil | Thermal oil/organics |  |  |  | Steam Rankine | [19 empty] | Abengoa | Spain | SpaceTube 8.2
NOOR II |  | 108 | Morocco | MENA | Operational | 200 | 600 |  | 34.25% | Parabolic Trough | 70 | 0.35 | Co-located PV; no economic hybridisation | 2015 | 2018 | Drâa-Tafilalet |  | Ouarzazate |  | 2503 | 1100 | USD | 2018 | 1119.2 | 5596 | 0.16 | 1.36 | MAD | 2018 | 0.14 | 25 | PPA |  | CTF $119 million; IBRD $119 million (Noor II and III) |  | ACWA | Saudi Arabia | NOMAC |  | ONE | Sener, SEPCO III | Spain, China |  |  | Thermal oil | Thermal oil/organics | Siemens | Germany | SST-500/SST-80 | Steam Rankine |  |  |  |  | Dry | 2-tank indirect | 7 | Molten salt |  |  | Rioglass | Spain |  |  |  | 293 | 393 |  |  | Sener | Spain | SenerTrough2 |  |  |  | 1779900 | 1.4832
NOOR III |  | 109 | Morocco | MENA | Operational | 150 | 500 |  | 38.05% | Power Tower | 70 | 0.46667 | Co-located PV; no economic hybridisation | 2017 | 2018 | Drâa-Tafilalet |  | Ouarzazate | 31.06,-6.87 | 2508 | 862 | USD | 2018 | 877.05 | 5847 | 0.15 | 1.42 | MAD | 2018 | 0.15 | 25 | PPA |  | CTF $119 million; IBRD $119 million (Noor II and III) |  | ACWA | Saudi Arabia | NOMAC |  | ONE | Sener, SEPCO III | Spain, China |  |  | Molten salt | Salt | Siemens | Germany | SST- 700/900 | Steam Rankine |  |  |  |  | Dry | 2-tank direct | 7 | Molten salt |  |  | Sener | Spain |  | 247 | [5 empty] | Sener | Spain | HE54 |  |  |  | 1312000 | 1.4578
Shouhang Dunhuang Phase II - 100 MW Tower | 北京首航艾启威节能技术股份有限公司敦煌熔盐塔式100兆瓦光热发电示范项目 | 110 | China | Asia | Operational | 100 | 483 |  | 55.14% | Power Tower |  |  |  | 2016 | 2018 | Gansu | Jiuquan | Dunhuang | 40.062,94.425 | 1777 | 3040 | RMB | 2018 | 458.15 | 4581.5 | 0.08 | 1.15 | RMB | 2018 | 0.17 | 20 | FIT | Chinese Demonstration Program 1st Batch |  | 8 | Shouhang | China | Shouhang |  | Gansu State Grid Electric Power | Suncan (Shouhang) | China | Jiaocheng Bingshen Chemical company | China | Molten Salt | Salt | GE | USA | N100-12.6/550/550 | Steam Rankine | 126 | 45 | Shandong Beichen Mechanical Electrical Equipment | China | Dry | 2-tank direct | 11 | Molten Salt | Shanghai Lanbin Petrochemical Equipment (LANPEC Technologies Limited) | China | Shouhang | China | External - cylindrical | 263 |  | 290 | 565 | Shouhang | China | Shouhang | China |  |  |  |  | 1400000 | 2.3333 | 12121 | 116 | [9 empty] | 1500 | 60 | http://www.cspfocus.cn/study/pdetail_206.htm; https://www.sohu.com/a/312422783_734062, http://web.archive.org/web/20201106104344/http://cspfocus.cn/market/detail_3333.htm
SUPCON Delingha 50 MW Tower | 青海中控太阳能发电有限公司德令哈熔盐塔式5万千万光热发电项目 | 111 | China | Asia | Operational | 50 | 146 |  | 33.33% | Power Tower |  |  |  | 2016 | 2018 | Qinghai | Haixi | Delingha | 37.366,97.293 | 2043 | 1050 | RMB | 2018 | 158.24 | 3164.8 | 0.09 | 1.15 | RMB | 2018 | 0.18 | 20 | FIT | Chinese Demonstration Program 1st Batch |  | 2.5 | SUPCON Solar | China | SUPCON Solar |  | Qinghai State Grid Electric Power | SUPCON solar | China | Zhejiang Lianda Chemical Company (supply of Sodium nitrate) | China | Molten Salt | Salt | Hangzhou Steam Turbine Company | China | N50-13.2/540/540 | Steam Rankine | 132 | 0.431 | Hangzhou Boiler Group | China | Dry | 2-tank direct | 7 | Molten salt | Bluestar (Beijing) Chemical Machinery Co., Ltd. | China | Hangzhou Boiler Group | China | External - cylindrical | 200 |  | 290 | 565 | Supcon | China | Supcon | China | SUPCON | Damin Glass | China |  | 542700 | 1.809 | 27135 | 20 | [9 empty] | 1500 | 70 | http://cnste.org/html/jiaodian/2017/1110/2223.html; http://www.cspplaza.com/article-12584-1.html
Xina Solar One |  | 112 | South Africa | Sub-Saharan Africa | Operational | 100 | 380 |  | 43.38% | Parabolic Trough |  |  |  | 2014 | 2018 | Northern Cape | Namakwa District Municipality | Pofadder | -28.892,19.591 | 2960 | 880 | USD | 2017 | 895.36 | 8953.6 | 0.2 | 1.9 | ZAR | 2017 | 0.15 | 20 | PPA |  | AfDB $141.5 million |  | Abengoa | Spain | Abengoa |  | Eskom | Abener | Spain |  |  | Thermal oil | Thermal oil/organics | Siemens | Germany |  | Steam Rankine |  |  |  |  | Dry | 2-tank indirect | 5.5 | Molten salt |  |  | Rioglass | Spain | UVAC 90 |  |  |  |  | Abengoa | Spain | Abengoa | Spain | SpaceTube 8.2 |  |  |  | 850000 | 1.4167
Ashalim Plot A /Negev Energy |  | 113 | Israel | MENA | Operational | 110 | 415 |  | 43.07% | Parabolic Trough |  |  | Co-located with Ashalim C PV (and Ashalim B) | 2015 | 2019 | Southern District |  | Ashalim | 30.967,34.684 | 2393 | 1000 | USD | 2017 | 1017.45 | 9249.6 | 0.21 | 0.76 | ILS | 2017 | 0.23 | 25 | PPA |  | Private Investment Corporation (OPIC), the European Investment Bank (EIB) 150 Mio Euro, Israel's Bank Leumi and Bank Hapoali |  | Abengoa, Shikun&Binui | Spain, Israel | Negev Energy, Noy Fund |  | Israel Electricity Corporation | TSK, Abengoa, Solel | Spain, Israel |  |  | Thermal oil | Thermal oil/organics |  |  |  | Steam Rankine | [5 empty] | 2-tank indirect | 4.5 | Molten salts |  |  | Rioglass | Spain | [5 empty] | Abengoa | Spain | Abengoa | Spain | E2 | Rioglass | Spain | [11 empty] | 10 |  |  | 633 | 60
Ashalim Plot B / Megalim |  | 114 | Israel | MENA | Operational | 121 | 320 |  | 30.19% | Power Tower |  |  | Co-located with Ashalim C PV (and Ashalim A) | 2015 | 2019 | Southern District |  | Ashalim | 30.962,34.728 | 2393 | 840 | USD | 2017 | 854.66 | 7063.3 | 0.23 | 0.79 | ILS | 2017 | 0.24 | 25 | PPA |  |  | 3.2 | Megalim Solar Power Ltd; (JV: BrightSource; GE Renewable Energy;Noy Fund) | USA | BrightSource Energy (25%) General Electric (25%) NOY Infrastructure & Energy Investment Fund (50%) |  | Israel Electricity Corporation | General Electric | USA |  |  | Water | Water |  |  |  | Steam Rankine | [10 empty] | General Electric (GE) | USA |  | 240 | [5 empty] | Brightsource | USA | LH-2.4 | AGC Glass Europe |  |  | 1052480 | 1.4497 | 50600 | 21
CEEC Hami - 50MW Tower | 中国电力工程顾问集团西北电力设计院有限公司哈密熔盐塔式5万千瓦光热发电项目 | 115 | China | Asia | Operational | 50 | 198.4 |  | 45.3% | Power Tower |  |  |  | 2017 | 2019 | Xinjiang (XUAR) | Hami | Yiwu | 43.613785, 94.956374 | 1789 | 1580 | RMB | 2017 | 238.12 | 4762.3 | 0.1 | 1.15 | RMB | 2017 | 0.17 | 20 | FIT | Chinese Demonstration Program 1st Batch |  | 4.4 | China Energy Engineering Corporation (CEEC), Dongfang Electric | China | China Energy Engineering Corporation (CEEC) |  | The State Grid Xinjiang Electric Power | Northwest Power Design Institute (NWEPDI) of CEEC | China | Jiaocheng Bingsheng Chemical | China | Molten Salt - Potassium nitrate | Salt | Dongfang Boiler | China | N50-14/550/550 | Steam Rankine | 140 | 44 | Dongfang | China | Dry (direct air) | 2-tank direct | 13 | Molten Salt | Bluestar (Beijing) Chemical Machinery Co., Ltd. | China | Dongfang | China | External - cylindrical | 220 |  | 290 | 560 | Wuham | China | Stellio Consortium(SBP) | Germany | Stellio | Wuhan Sunnpo Solar Technology Co.,Ltd. | China |  | 696751 | 2.3225 | 14500 | 50 | [9 empty] | 1200 | 50 | http://www.cspfocus.cn/en/study/detail_66.htm; https://www.solarpaces.org/a-novel-csp-heliostat-goes-from-lab-to-market-in-just-5-years/;https://www.sohu.com/a/313134566_120093798;https://www.xianjichina.com/special/detail_400359.html; https://web.archive.org/web/20210705132541/http://www.cnste.org/html/xiangmu/2021/0621/8026.html; https://web.archive.org/web/20220715081902/https://cspplaza.com/article-20708-1.html
Lanzhou Dacheng Dunhuang (DCTC Dunhuang) - 50MW Fresnel | 兰州大成科技股份有限公司敦煌熔盐线性菲涅尔式5万千瓦光热发电示范项目 | 116 | China | Asia | Operational | 50 | 214 |  | 48.86% | Linear Fresnel |  |  |  | 2018 | 2020 | Gansu | Jiuquan | Dunhuang | 40.084,94.421 | 1649 | 1688 | RMB | 2017 | 253.19 | 5063.7 | 0.1 | 1.15 | RMB | 2017 | 0.17 | 20 | FIT | Chinese Demonstration Program 1st Batch | Power China Leasing Co., Ltd (debt funding), China Agricultural Development Bank Dunhuang Sub-branch and Gansu Financial Holding Group | 3.2 | Dunhuang Dacheng Concentrating Thermal Power Co. (Lanzhou Dacheng Technology Co., Ltd) | China | Dunhuang Dacheng Concentrating Thermal Power Co. (Lanzhou Dacheng Technology Co., Ltd) |  | State Grid Gansu Electric Power Company | Lanzhou Dacheng Concentrating Energy Technology (Lanzhou Dacheng Technology Co., Ltd) | China |  |  | Molten salt | Salt | Dongfang Boilor | China |  | Steam Rankine | [5 empty] | 2-tank direct | 15 | Molten Salt | Shanghai Lanbin Petrochemical Equipment (LANPEC Technologies Limited) | China | Lanzhou Dacheng Vacuum Technology Co. (Lanzhou Dacheng Technology Co., Ltd) | China |  |  |  | 290 | 550 |  |  | Lanzhou Dacheng | China |  | Daming Glass | China |  | 1270000 | 4.2333 |  |  |  | 80 | 1100 | [6 empty] | 1300 |  | http://www.cspplaza.com/article-16244-1.html; http://www.cnste.org/html/xiangmu/2019/1231/5897.html;https://www.sohu.com/a/306798669_120093798;http://www.cspfocus.cn/market/detail_2831.htm; http://web.archive.org/web/20201106104344/http://cspfocus.cn/market/detail_3333.htm
eLLO Solar Thermal Project |  | 117 | France | Europe | Operational | 9 | 20.2 |  | 25.62% | Linear Fresnel |  |  |  | 2016 | 2019 | Occitanie |  | Llo | 42.469,2.063 | 1930 | [10 empty] | 20 |  | French tender for solar energy |  | 0.35 | eLLO (51% SUNCNIM - 49% Caisse des Dépôts et Consignations) | France | eLLO | SUNCNIM | EDF |  |  |  |  | Water | Water |  |  |  |  | 70 |  |  |  | Dry | Other | 3 | Steam drum |  |  | SUNCIM | France |  |  |  | 190 | 285 | [8 empty] | 153000 | 2.8333 |  |  | 14 | 27 | 340
ISCC Green Duba 1 |  | 118 | Saudi Arabia | MENA | Under Construction | 43 |  |  |  | ISCC; Trough | 605 | 14.0698 | ISCC | 2016 | 2023 | Tabuk |  | Duba | 27.7486,35.451 | 2469 | [15 empty] | Saudi Electriciy Company | Saudi Arabia | Saudi Electriciy Company |  | Saudi Electricity Co. | Initec Energia; Saudi Services For Electro Mchanic Works | Spain; Saudi Arabia |  |  | Thermal Oil | Thermal oil/organics |  |  |  | Steam Rankine | [10 empty] | Archimede Solar Energy | Italy | [7 empty] | SBP | Germany | Ultimate Trough | Flabeg | Germany | [16 empty] | https://www.power-technology.com/marketdata/duba-green-al-wajh-line-saudi-arabia/; https://web.archive.org/web/20230504223017/https://www.zawya.com/en/projects/utilities/saudis-green-duba-iscc-project-to-be-ready-for-handover-in-q3-2023-mboujqcf
Kathu Solar Park |  | 119 | South Africa | Sub-Saharan Africa | Operational | 100 | 500 |  | 57.08% | Parabolic Trough |  |  |  | 2016 | 2019 | Northern Cape | John Taolo Gaetsewe District Municipality | Kathu | -27.734,23.063 | 2830 | 12000 | ZAR | 2019 | 917.86 | 9178.6 | 0.16 | 1.8 | ZAR | 2019 | 0.14 | 20 | PPA |  |  | 4.5 | Engie | France | Kathu Solar Park Consortium |  | Eskom | Acciona, Sener | Spain |  |  | Thermal Oil | Thermal oil/organics |  |  |  | Steam Rankine |  |  |  |  | Dry | 2-tank indirect | 5 | Molten salt |  |  | Rioglass | Spain |  |  |  | 293 | 393 |  |  | Sener | Spain | SenerTrough2
LuNeng Haixi - 50MW Tower | 鲁能海西州50MW塔式光热发电项目 | 120 | China | Asia | Operational | 50 | 160 |  | 36.53% | Power Tower | 600 | 12 | Multi energy complex: 400 MW wind power, 200 MW photovoltaic, 50 MW of CSP, and 50 MW energy storage | 2017 | 2019 | Qinghai | Haixi | Golmud | 36.397,95.227 | 1945 | 1100 | RMB | 2019 | 165.78 | 3315.5 | 0.09 |  |  |  |  | 20 |  | First batch of complementary multi-energy demonstration projects |  | 4.3 | Luneng Qinghai Guangheng New Energy (Luneng Group of State Grid) | China | Luneng Group (State Grid) |  | Qinghai State Grid Electric Power | SEPCO III | China | Qinghai Lianda Chemical Company |  | Molten Salt | Salt | Siemens | Germany |  | Steam Rankine | [5 empty] | 2-tank direct | 12 | Molten Salt | Empyro |  | Cockerill | Belgium | External - cylindrical | 188 |  |  |  | Abengoa | Spain | Abengoa | Spain | ASUP 140 | Damin Glass | China |  | 610000 | 2.0333 | 4400 | 138 | [11 empty] | http://www.cspplaza.com/article-12674-1.html
Power China Qinghai Gonghe - 50MW Tower | 中国电建西北勘测设计研究院有限公司共和熔盐塔式5万千瓦光热发电项目 | 121 | China | Asia | Operational | 50 | 157 |  | 35.84% | Power Tower |  |  |  | 2017 | 2019 | Qinghai | Hainan | Gonghe | 36.102,100.625 | 1883 | 1222 | RMB | 2017 | 184.16 | 3683.3 | 0.1 | 1.15 | RMB | 2017 | 0.17 | 20 | FIT | Chinese Demonstration Program 1st Batch |  | 2.1 | Northwest Engineering Corporation (Power China) | China | HYDROCHINA and Northwest Engineering Corporation (Power China) |  | State Grid Qinghai Electric Power company | Northwest Engineering Corporation (Power China) | China | Qinghai Lianda Chemical Company | China | Molten salt | Salt | Harbin Turbine Company | China |  | Steam Rankine |  |  | HollySys Automation Technologies | China | Dry | 2-tank direct | 6 | Molten Salt | Bai Ji Rui (Tianjin) New Energy & Emypro S.A. | China | Hangzhou Boiler Group | China |  | 210 |  | 290 | 565 | Supcon | China | Supcon | China | SUPCON | Damin Glass | China |  | 516000 | 1.72 | 25795 | 20 | [11 empty] | http://www.cspfocus.cn/en/study/pdetail_391.htm; http://www.cspplaza.com/article-16136-1.html; https://www.sohu.com/a/292389028_734062
Shagaya CSP Project |  | 122 | Kuwait | MENA | Operational | 50 | 180 |  | 41.1% | Parabolic Trough | 10 | 0.2 | Co-located PV; no economic hybridisation; Fuel-oil burner | 2017 | 2019 |  |  | Kuwait City | 29.139,47.018 |  | 116 | KWD |  |  |  |  | 0.16 | USD | 2017 | 0.17 | 25 | PPA |  | "Financed by the government" |  | Kuwait Institute for Scientific Research | Kuwait | Kuwait Institute for Scientific Research | TSK |  | TSK; Kharafi National | Spain, Kuwait |  |  |  |  | Siemens | Germany | SST-700 RH | Steam Rankine |  |  |  |  | Dry | 2-tank indirect | 9 | Molten salt |  |  | Schott | Germany | [5 empty] | TSK | Spain | SBP, Flagsol | Germany | SKAL ET-150 | Rioglass | Spain
Atacama I / Cerro Dominador 110MW CSP + 100 MW PV |  | 123 | Chile | South America | Operational | 110 |  |  |  | Power Tower | 100 | 0.90909 | Co-located with PV; project level hybridisation | 100 | 2021 | Antofagasta |  | Calama | -22.771,-69.479 | 3186 | 1400 | USD | 2017 | [8 empty] | PPA |  | Inter-American development bank, World bank CTF, KfW (100 million €), EU (15 million €) | 7 | Abengoa | Spain | EIG | Abengoa Solar | Sistema Interconectado del Norte Grande (SING) | Abengoa, Acciona | Spain |  |  | Molten Salt | Salt | Doosan Skoda Power | Czechia |  | Steam Rankine |  |  |  |  | Dry | 2-tank direct | 17.5 | Molten salt |  |  | Cockerill | Belgium |  | 243 |  |  |  | Abengoa | Spain | Abengoa | Spain | ASUP 40V3 | Rioglass | Spain |  | 1484000 | 2.2485 | 10600 | 140 | [11 empty] | https://www.reuters.com/business/energy/eig-global-launches-thermal-solar-project-chile-latams-first-2021-06-08/
CSNP Urat - 100MW Trough | 内蒙古中核龙腾新能源有限公司乌拉特中旗导热油槽式10万千瓦光热发电项目 | 124 | China | Asia | Operational | 100 | 350 |  | 39.95% | Parabolic Trough |  |  |  | 2017 | 2020 | Inner Mongolia | Bayannur | Urat Middle Banner | 41.507, 108.588 | 2170 | 2800 | RMB | 2017 | 421.98 | 4219.8 | 0.1 | 1.15 | RMB | 2017 | 0.17 | 20 | FIT | Chinese Demonstration Program 1st Batch |  | 4.7 | RoyalTech | China | Inner Mongolia RoyalTech New Energy Co., Ltd. (JV Royaltech and China Nuclear (Nanjing) Energy Development Co., Ltd) |  | Inner Mongolia Power company | China Shipbuilding New Power (CSNP) | China | Jiangsu Zhongneng; China shipbuilding corporation | China | Thermal oil | Thermal oil/organics | Siemens | Germany |  | Steam Rankine |  |  | Wuxi Chemical | China | Dry | 2-tank indirect | 10 | Molten Salt | Shanghai Lanbin Petrochemical Equipment (LANPEC Technologies Limited), East China Engineering Science and Technology Co., Ltd. (ECEC), | China | RoyalTech | China | [5 empty] | Royal Tech CSP | China | SBP | Germany | ET-150 | Riohuan (JV of Rioglass & Zhonghuan); Sundhy (Chengdu) Solar Power Co., Ltd | China |  | 1150000 | 1.9167 | [6 empty] | 150 | 352 | 12 |  |  |  |  | http://helioscsp.com/1365-receiver-tubes-sent-to-china-cnnc-royal-tech-urad-100mw-parabolic-trough-concentrated-solar-power-project/; http://www.cspfocus.cn/en/study/detail_74.htm;https://www.sbp.de/en/project/parabolic-trough-power-plant-urat/ http://www.cspplaza.com/article-8085-1.html
Yumen Xinneng / Xinchen - 50MW Beam-down | 玉门鑫能光热第一电力有限公司熔盐塔式5万千瓦光热发电项目 | 125 | China | Asia | Operational | 50 | 72 |  | 16.44% | Beam-Down Tower |  |  |  | 2017 | 2021 | Gansu | Jiuquan | Yumen | 40.338,97.276 | 1641 | 1790 | RMB | 2017 | 269.76 | 5395.3 |  | 1.15 | RMB | 2017 | 0.17 | 20 | FIT | Chinese Demonstration Program 1st Batch |  | 3.69 | China Sinogy Electric Engineering Co., Ltd (NREL: Shanghai Parasol Renewable Energy Company and Jiangsu Xinchen CSP Co., Ltd) | China | Yumen Xinneng Thermal Power Co., Ltd owned by Thvom (Shanghai electric: 15% ownership of Thvom) | SUZHOU THVOW TECHNOLOGY CO.,LTD | Gansu Branch of State Grid Electric Power | China Sinogy Electric Engineering Co., Ltd | China | Hualong Ammonium Nitrate Co; Shadong Ocean Chemical | China | Sodium Nitrate | Salt | Shanghai Turbine Works (Shanghai electric) | China |  | Steam Rankine | 140 | 43.7 | Dongfang Boiler | China | Dry | 2-tank direct | 9 | Molten Salt | Jiangsu XinChen | China | Jiangsu XinChen | China | Beamdown Receiver T1 | 70 | 5 | 290 | 570 | Jiangsu Xinchen | China | Jiangsu XinChen | China | P3 | Taiwan Glass Yueda Solar Mirror Co. Ltd. | China |  | 208240 | 0.69413 | 13015 | 16 | [9 empty] | 1500 | 52 | http://www.cspfocus.cn/report/detail_40.htm; http://www.cnste.org/html/xiangmu/2021/0320/7682.html, http://www.cnste.org/html/xiangmu/2021/0423/7828.html
Noor Energy 1 / DEWA IV - 100MW tower segment |  | 126 | United Arab Emirates | MENA | Operational | 100 |  |  |  | Power Tower |  |  | Co-located with 250 MW PV and 600 MW CSP trough for a total of 950 MW; project level hybridsiation | 2018 | 2023 | Dubai |  | Dubai | 24.76,55.36 | 1967 |  |  | 2017 | [12 empty] | ACWA, Shanghai Electric | Saudi Arabia, China | Dubai Electricity & Water Authority | NOMAC | Dubai Electricity & Water Authority | Shanghai Electric | China | BASF | Germany | Molten Salt | Salt | Siemens | Germany |  | Steam Rankine | [5 empty] | 2-tank direct | 15 | Molten salt | Shanghai Lanbin Petrochemical Equipment (LANPEC Technologies Limited) | China | Cockerill, Shanghai Boiler Work | Belgium, China |  | 260 | [5 empty] | Brightsource | USA | LH-2.5 | AGC Glass | Japan | AGC SunMax Reflect |  |  | 70000 | [12 empty] | http://web.archive.org/web/20201001133420/https://img03.en25.com/Web/FCBusinessIntelligenceLtd/%7Beabe1801-9654-4e8e-92a2-eef0f5034ff4%7D_5027_11JUN19_Whitepaper.pdf; https://acwapower.com/media/341814/acwa_power_annual_report_2021_en.pdf; https://www.zawya.com/en/projects/utilities/dubai-solar-power-plants-100mw-central-tower-is-operational-acwa-power-p6zwwkq3
Noor Energy 1 / DEWA IV 3x 200MW trough segment |  | 127 | United Arab Emirates | MENA | Under Construction | 600 |  |  |  | Parabolic Trough |  |  | Co-located with 250 PV and a 100 MW CSP tower for a total of 950 MW; project level hybridsiation | 2018 | 2023 | Dubai |  | Dubai | 24.76,55.36 | 1967 |  |  | 2017 | [12 empty] | ACWA, Shanghai Electric | Saudi Arabia, China | Dubai Electricity & Water Authority | NOMAC | Dubai Electricity & Water Authority | Shanghai Electric | China | Dow | USA | Biphenyl/Diphenyl oxide: Dowtherm A | Thermal oil/organics | Siemens | Germany |  | Steam Rankine | [5 empty] | 2-tank indirect | 11 | Molten salt | Shanghai Lanbin Petrochemical Equipment (LANPEC Technologies Limited) | China | Rioglass | Spain | PTR 90-4G |  |  |  |  | Abengoa | Spain | Abengoa | Spain | SpaceTube 8.2 | Rioglass | Spain | 8.2 | [15 empty] | http://web.archive.org/web/20201001133420/https://img03.en25.com/Web/FCBusinessIntelligenceLtd/%7Beabe1801-9654-4e8e-92a2-eef0f5034ff4%7D_5027_11JUN19_Whitepaper.pdf; https://acwapower.com/media/341814/acwa_power_annual_report_2021_en.pdf; https://www.dow.com/en-us/insights-and-innovation/product-news/dow-and-shanghai-electric-collaborate-on-a-world-scale-concentrated-solar-power-project
CSP-PV hybrid project Noor Energy 1 / DEWA IV |  | 128 | United Arab Emirates | MENA | Under Construction |  |  |  |  | PV-Hybrid; Trough; Tower | 250 | 0.35714 | Project level hybridisation of PV and CSP | 2018 | 2023 | Dubai |  | Dubai | 24.76,55.36 | 1967 | 14780 | AED | 2017 |  |  |  | 0.27 | AED | 2017 | 0.073 | 35 | PPA |  | $4.4 billion cost of Noor Energy 1 will be met by $2.9 billion of debt and $1.5 billion of equity. DEWA is to provide $750 million, half of the project equity. Of the remaining half, ACWA Power will provide 51% and China's Silk Road Fund 49%. Over 70% of the project debt will come from Chinese banks including Industrial and Commercial Bank of China Limited (ICBC), with the remainder supplied by international and regional banks. |  | ACWA, Shanghai Electric | Saudi Arabia, China | Dubai Electricity & Water Authority | NOMAC | Dubai Electricity & Water Authority | Shanghai Electric | China
Dadri ISCC Plant |  | 129 | India | Asia | Operational | 14 | 14 |  | 11.42% | ISCC; Fresnel | 210 | 15 | ISCC | 2016 | 2019 | Uttar Pradesh |  | Dadri | 28.578,77.632 | 1223 | [15 empty] | Frenell | Germany | NTCP |  | NTCP | Thermax | India |  |  | Water/Steam | Water |  |  |  | Steam Rankine | [10 empty] | Royal Tech | China |  |  |  |  | 250 |  |  | Frenell | Spain, Germany |  |  |  |  | 33000 | 0.39286 |  |  |  | 0 | [9 empty] | http://web.archive.org/web/20190716153855/http://en.cspplaza.com/asias-first-integrated-solar-thermal-power-plant-is-now-online
Sierra SunTower |  | 130 | United States | North America | Currently Non-Operational | 5 |  |  |  | Power Tower | [5 empty] | California |  | Lancaster | 34.731,-118.139 | [14 empty] | Expected 30% Federal Investment Tax Credit (ITC, 5-year MACRS) |  | eSolar | USA | eSolar | eSolar | Southern California Edison |  |  |  |  | Water | Water |  |  |  | Steam Rankine |  |  |  |  | Wet | [5 empty] | Babcock & Wilcox |  | External - Dual-cavity receiver & tubular external receiver | 55 | [5 empty] | eSolar | USA |  |  |  |  | 27670 | 0.92233 | 24360 | 1 | [9 empty] | 130 | 12
Tooele Army Depot |  | 131 | United States | North America | Currently Non-Operational | 1.5 |  |  |  | Dish |  |  |  | 2012 |  | Utah | Tooele County | Tooele | 40.501,-112.374 | [15 empty] | 0.07 | Infinia | USA | Tooele Army Depot | [6 empty] | Helium |  |  |  |  | Stirling | [19 empty] | Infinia Corp | PowerDish 3.5KW | [6 empty] | 429
Solar One |  | 135 | United States | North America | Decommissioned | 10 |  |  |  | Power Tower |  |  |  |  | 1982 | California |  | Daggett | 34.871,-116.834 | 2885 | [14 empty] | 0.51 | Sandia National Laboratories | USA | [7 empty] | Steam | [18 empty] | 90 | [11 empty] | 72650 | 1.2108 | 1818 | 40 | [11 empty] | https://www.nrel.gov/docs/fy01osti/28751.pdf, http://web.archive.org/web/20210707091436/https://www.nrel.gov/docs/legosti/fy97/22835.pdf
Solar Two |  | 136 | United States | North America | Decommissioned | 10 |  |  |  | Power Tower |  |  |  |  | 1995 | California |  | Daggett | 34.871,-116.834 | 2885 | [15 empty] | Sandia National Laboratories | USA | [7 empty] | Molten Salt | [11 empty] | 3 | [33 empty] | https://www.nrel.gov/docs/fy01osti/28751.pdf, http://web.archive.org/web/20210707091436/https://www.nrel.gov/docs/legosti/fy97/22835.pdf
National Solar Thermal Test Facility |  | 137 | United States | North America | Operational | 5 |  |  |  | Power Tower |  |  |  |  | 1976 | New Mexico |  | Albuquerque | [17 empty] | Sandia National Laboratories | USA | [26 empty] | 63 | [13 empty] | 222 | [12 empty] | https://www.nrel.gov/docs/fy01osti/28751.pdf
CRS Sales |  | 138 | Spain | Europe | Operational | 5 |  |  |  | Power Tower |  |  |  |  | 2012 | Andalusia | Sevilla | Sevilla | [17 empty] | Abengoa | Spain | [7 empty] | Molten Salt | Salt | [19 empty] | 290 | 565 | Abengoa | Spain | Abengoa | Spain |  |  |  |  | 10560 | 0.352 | 88 | 120 | [11 empty] | https://doi.org/10.1016/j.egypro.2014.03.052
SEDC |  | 139 | Israel | MENA | Operational | 6 |  |  |  | Power Tower |  |  |  |  | 2008 | [20 empty] | Brightsource | USA | [7 empty] | Steam | Water | [17 empty] | 60 |  |  | 540 | [10 empty] | 1600 | [12 empty] | http://web.archive.org/web/20210706101300/https://s7.addthis.com/js/300/addthis_widget.js
Solar Heat and Power Liddell |  | 140 | Australia | Australia | Currently Non-Operational | 1 |  |  |  | Linear Fresnel |  |  |  |  | 2004 | New South Wales |  | Liddell | -32.376,150.98 | [16 empty] | Solar Heat and Power |  | Ausra | [6 empty] | Water | Water | [33 empty] | 1.82 | [10 empty] | https://www.researchgate.net/publication/242170632_First_Results_from_Compact_Linear_Fresnel_Reflector_Installation
Kimberlina Solar Thermal Power Plant |  | 142 | United States | North America | Currently Non-Operational | 5 |  |  |  | Linear Fresnel |  |  |  | 2008 | 2008 | California |  | Bakersfield | 35.566,-119.194 | [15 empty] | 0.05 | Ausra | Australia | Ausra | Ausra | California ISO | [9 empty] | Steam Rankine | 40 | [16 empty] | Ausra | Australia | [6 empty] | 25988 | 0.86627 |  |  | 2 | 3 | 385
Jinta Zhongguang Solar 100 MW Tower + 600 MW PV | 金塔中光10万千瓦光热+60万千瓦光伏项目 | 143 | China | Asia | Under Construction | 100 | 209 | 1370 | 23.86% | PV-Hybrid; Tower | 600 | 6 | Co-located with 600 MW PV | 2022 | 2023 | Gansu | Jiuquan | Jinta | 40.06, 98.67 |  | 4130 | RMB | 2022 |  |  |  | 0.3078 | RMB | 2021 | 0.05 |  | FIT | Subsidy free, supported by provincial coal tariff. |  | 3.62 | Jinta ZhongGuang Solar Power Generation Co., Ltd., and Cosin for CSP | China |  |  | Gansu State Grid Electric Power | CEEC | China |  |  | Molten Salt | Salt | Shanghai Turbine Works (Shanghai electric) | China |  | Steam Rankine | [6 empty] | 9 | Molten Salt | Bluestar (Beijing) Chemical Machinery Co., Ltd. | China |  |  |  | 220 |  |  |  | Cosin Solar (Supcon) | China | Cosin Solar (Supcon) | China |  |  |  |  | 767820 | 1.2797 | [13 empty] | https://www.solarpaces.org/cosin-breaks-ground-on-100-mw-csp-and-thermal-storage-in-gansu-province/, https://web.archive.org/web/20220711161449/http://www.cspfocus.cn/en/market/detail_5634.htm; http://web.archive.org/web/20230327124259/https://www.solarpaces.org/wp-content/uploads/Blue-Book-on-Chinas-CSP-Industry-2021.pdf; https://www.solarpaces.org/cosin-breaks-ground-on-100-mw-csp-and-thermal-storage-in-gansu-province/; http://www.cnste.org/html/xiangmu/2022/0826/9392.html; https://web.archive.org/web/20230627152440/http://www.cosinsolar.com/upload/file/2023-06/1686055421871457.pdf
Redstone |  | 144 | South Africa | Sub-Saharan Africa | Under Construction | 100 | 466 |  | 53.2% | Power Tower |  |  | Co-located with the 75 MW Jasper and 96 MW Lesedi PV Projects (SolarReserve) | 2021 | 2023 | Northern Cape |  | Potmasburg | -28.298476,23.368182 |  | 116000 | ZAR | 2020 | 704.22 | 7042 | 13 | [9 empty] | ACWA, SolarReserve | Saudi Arabia, United States |  |  | Eskom | SEPCO III | China | [14 empty] | 12 | Molten salt | Shanghai Lanbin Petrochemical Equipment (LANPEC Technologies Limited) | China | Cockerill | Belgium |  | 250 | [5 empty] | Brightsource | USA | LH-2.5 | [5 empty] | 41260 | [10 empty] | 2000 | 100 | https://www.trinityllp.com/redstone-csp-reaches-financial-close/; https://acwapower.com/media/341814/acwa_power_annual_report_2021_en.pdf; https://johncockerill.com/wp-content/uploads/2021/07/20210715-Redstone-CSP-John-Cockerill-ACWA-Power-PressRelease.pdf
CEIC Dunhuang 100 MW Fresnel + 600 MW PV | 敦煌70万千瓦“光热储能+光伏”试点项目 | 145 | China | Asia | Under Construction | 100 |  | 1530 | 174.7% | PV-Hybrid; Fresnel | 600 | 6 | Co located with 600 MW PV | 2021 | 2024 | Gansu | Jiuquan | Dunhuang |  | 1649 | 4300 | RMB | 2022 |  |  |  | 0.3078 | RMB | 2021 | 0.05 |  | FIT | Subsidy free, supported by provincial coal tariff. |  | 14.3 | China Energy Group Longyuan Power Gansu Company | China |  |  | Gansu State Grid Electric Power |  |  |  |  | Molten Salt | Salt | [11 empty] | Molten Salt |  |  | Lanzhou Dacheng Vacuum Technology Co. (Lanzhou Dacheng Technology Co., Ltd) | China | [7 empty] | Lanzhou Dacheng | China | [19 empty] | https://web.archive.org/web/20220715095002/https://cspplaza.com/article-20866-1.html
Huidong New Energy Akesai 110MW + 640MW PV | 阿克塞汇东新能源有限公司75万千瓦光热+示范项目 | 146 | China | Asia | Under Construction | 110 |  | 1700 | 176.4% | PV-Hybrid; Tower | 640 | 5.8182 | Co located with 640 MW PV | 2022 | 2023 | Gansu | Jiuquan | Aksai |  |  | 5060 | RMB | 2021 |  |  |  | 0.3078 | RMB | 2021 | 0.05 |  | FIT | Subsidy free, supported by provincial coal tariff. |  | 3.15 | Huidong New Energy | China |  |  | Gansu State Grid Electric Power | East China Electric Power Design Institute (ECEPDI) of CEEC | China |  |  |  |  | Shanghai Turbine Works (Shanghai electric) | China |  | Steam Rankine |  |  | Shanghai Electric | China | Dry |  | 8 | Molten salt | Shanghai Lanbin Petrochemical Equipment (LANPEC Technologies Limited) of Sinomach | China | [9 empty] | Jiangsu XinChen (BCP Solar), Shanghai electric | China | Stellio |  |  |  | 581068 | 0.88041 | 23920 | 24.3 | [11 empty] | http://www.cnste.org/html/jiaodian/2022/0606/9065.html, http://en.cnste.org/html/news/2022/0617/1231.html; http://www.cspfocus.cn/en/market/detail_5597.htm; https://www.cspplaza.com/article-22777-1.html; http://web.archive.org/web/20230327123709/https://www.cspplaza.com/article-22777-1.html; https://web.archive.org/web/20230626090134/https://mp.weixin.qq.com/s/meW7SwoBuCb9V6hlDHPrgw
CSP2 Sicily Partanna MS-LFR |  | 147 | Italy | Europe | Operational | 4.26 |  |  |  | PV-Hybrid; Fresnel | 5.6 | 1.3146 | 5.6 PV, Natural gas boiler (2MW) |  | 2021 | Sicily | Trapani | Partanna |  | 1800 | [6 empty] | 0.311 | EURO |  |  |  | FIT | Italian CSP FIT |  |  |  |  | Sol.In.Par |  |  | Fata (Danieli Group) | Italy |  |  | Molten Salt | Salt | Tosi | Italy |  | Steam Rankine |  |  | Lointek | Spain |  | 2-tank direct | 15 |  |  |  | Archimede | Italy |  |  |  |  | 545 | Frenell | Italy | FRENELL | Spain |  |  |  |  | 83200 |  |  |  | 34 | 9 | 800 | [8 empty] | https://aip.scitation.org/doi/pdf/10.1063/5.0029269; https://www.fatagroup.it/solinpar-csp-plant-in-partanna-sicily-entered-into-production/; https://web.archive.org/web/20201127200313/https://www.qualenergia.it/articoli/solare-termodinamico-due-nuovi-impianti-in-sicilia/
SOLINPAR Sicily Stromboli MS-LFR |  | 148 | Italy | Europe | Under Construction | 4 |  |  |  | PV-Hybrid; Fresnel |  |  | PV | 2020 |  | Sicily |  |  | 37.91, 12.58 | 1800 | [6 empty] | 0.311 | EURO |  |  |  | FIT | Italian CSP FIT | [7 empty] | Fata (Danieli Group) | Italy |  |  | Molten Salt | Salt | [10 empty] | 16 |  |  |  | Huiyin | China | [7 empty] | SUNCNIM | France | [19 empty] | https://helioscsp.com/enea-alliance-and-industry-for-two-new-concentrated-solar-power-plants-in-sicily/
Three Gorges CTGR Henderson Energy Guazhou 2x50MW Tower + 200 MW PV + 400 MW Wind | 三峡恒基能脉瓜州70万千瓦“光热+”项目 | 149 | China | Asia | Under Construction | 100 |  | 1800 | 205.5% | Wind-PV-Hybrid; Tower | 600 | 6 | 2x50MW tower with one turbine, Co-located with 200 MW PV and 400 MW Wind | 2022 | 2024 | Gansu | Jiuquan | Qiaowan, Guazhou | 40.59, 96.46 |  | 4930 | RMB | 2022 |  |  |  | 0.3078 | RMB | 2021 | 0.05 |  | FIT | Subsidy free, supported by provincial coal tariff. |  |  | Three Gorges and Hernderson Energy | China | 51% Henderson New Energy Technology Co., Ltd. And China Three Gorges New Energy (Group) Co., Ltd. 49%. |  | Gansu State Grid Electric Power | China Energy Construction Gezhouba Electric Power of CEEC | China |  |  | Molten Salt | Salt | Harbin Electric | China |  | Steam Rankine | [10 empty] | Harbin Electric Boiler | China |  | 200.5 | [5 empty] | Hengji Nengmai | China | [6 empty] | 26964 | [12 empty] | http://web.archive.org/web/20230327124259/https://www.solarpaces.org/wp-content/uploads/Blue-Book-on-Chinas-CSP-Industry-2021.pdf
CNNC Yumen 100 MW Fresnel + 400 MW PV + 200 Wind | 玉门新奥70万千瓦光热储能+光伏+风电示范项目 | 150 | China | Asia | Under Construction | 100 |  | 1760 | 200.9% | Wind-PV-Hybrid; Fresnel | 600 | 6 | Co-located with 400 MW PV and 200 MW Wind | 2022 | 2023 | Gansu | Jiuquan | Yumen |  | 1641 | 5000 | RMB | 2022 |  |  |  | 0.3078 | RMB | 2021 | 0.05 |  | FIT | Subsidy free, supported by provincial coal tariff. |  |  | Northwest Electric Power Design Institute (NWEPDI), Dunhuang Dacheng Shengneng New Energy Technology | China | Yumen Xin’ao New Energy Co., Ltd., a joint venture of Gansu Bocheng Tongda Energy Co., Ltd and and Shaanxi Xinhua Water Conservancy and Hydropower Investment Co., Ltd., the latter a subsidiary of CNNC Xinhua Hydropower Co. Ltd |  | Gansu State Grid Electric Power | NWEPDI of CEEC | China |  |  | Molten Salt | Salt |  |  |  | Steam Rankine | [6 empty] | 8 | Molten Salt | Bluestar (Beijing) Chemical Machinery Co., Ltd. | [10 empty] | Lanzhou Dacheng | China |  |  |  |  | 1300000 | 2.1667 | [13 empty] | http://web.archive.org/web/20230403102834/http://www.cnste.org/html/xiangmu/2022/0308/8762.html; https://web.archive.org/web/20230623094719/https://mp.weixin.qq.com/s/vh7YZ_-Tb6A_y0b8X4f-dA; https://web.archive.org/web/20230623101419/https://mp.weixin.qq.com/s?__biz=MzUzNTQ0ODU3Mg==&mid=2247508591&idx=3&sn=1f68a0cf92c45f03ab1c8ac813db95e4&chksm=fa87bcfccdf035ea7c7e3300f72dc3c76282c016f1d472e70c026b021cdffe701499c146199d&scene=21
Power China Toksun 100 MW Tower + 900 MW PV |  | 151 | China | Asia | Under Construction | 100 |  | 1700 | 194.1% | PV-Hybrid; Tower | 900 | 9 | Co-located with 900 MW PV | 2023 |  | Xinjiang (XUAR) | Turpan | Toksun |  |  | 5710 | RMB | 2023 | [11 empty] | 2.5 | Power China | China |  |  |  | Zhongnan Survey and Design Research Institute of Power China | China |  |  | Molten Salt | Salt | [10 empty] | 8 | Molten Salt | [17 empty] | 440400 | 0.734 | 14680 | 30 | [11 empty] | http://web.archive.org/web/20230623133934/https://helioscsp.com/powerchina-new-energy-toksun-100-mw-tower-concentrated-solar-power-project-steam-turbine-generator-set-steam-generation-system-started-procurement/; http://www.cnste.org/html/xiangmu/2023/0603/10784.html
Power China Ruoqiang 100 MW Tower + 900 MW PV | 于若羌县铁木里克乡的中电建新能源若羌10万千瓦光热（储能）+90万千瓦光 | 152 | China | Asia | Under Construction | 100 |  | 2113 | 241.2% | PV-Hybrid; Tower | 900 | 9 | Co-located with 900 MW PV | 2022 | 2024 | Xinjiang (XUAR) | Bayingolin | Ruoqiang | 38.15, 90.11 |  | 1346(CSP) 5600(total) | RMB | 2022 | [11 empty] | 18.8 | Power China | China |  |  |  | China Water Conservancy and Hydropower First Engineering Bureau; Jiangxi Provincial Electric Power Design Institute (JXEPDI); Sepco III of Power China | China |  |  | Molten Salt | Salt | [10 empty] | 8 | Molten Salt | [11 empty] | SEPCO III | China |  |  |  |  | 600000 |  | 12371 | 48.5 | [9 empty] | 2000 | 200 | https://web.archive.org/web/20230623140358/https://mp.weixin.qq.com/s?__biz=MzUzNTQ0ODU3Mg==&mid=2247508806&idx=2&sn=d1da78e901330835728f20091a34ff9f&chksm=fa87bdd5cdf034c39c89ecf51084bc7923e84f6f4da2ebae7f88dde3508a17dcb79608b8dae0&scene=132; https://web.archive.org/web/20230626101335/https://mp.weixin.qq.com/s/sOZkUem9hSllsw29zrdRew; https://web.archive.org/web/20230627143738/https://www.cspplaza.com/article-22697-1.html; https://web.archive.org/web/20230629092711/https://m.sohu.com/a/692511550_120093798?_trans_=010004_pcwzy
SDIC Ruoqiang 100 MW Tower + 900 MW PV | 国投若羌10万千瓦光热发电项目 | 153 | China | Asia | Under Construction | 100 | 150.6 |  | 17.19% | PV-Hybrid; Tower | 900 | 9 | Co-located with 900 MW PV, Cost, generation, etc are here listed for the tower only | 2023 |  | Xinjiang (XUAR) | Bayingolin | Ruoqiang |  |  | 1690 (CSP) 5650 (total) | RMB | 2022 | [12 empty] | State Development and Investment Corporation (SDIC) | China |  |  |  | North China Electric Power Design Institute (NCEPDI) of CEEC, Shouhang Hi-Tech | China |  |  | Molten Salt | Salt | Dongfang | China | [21 empty] | Shouhang | China | [17 empty] | 2000 |  | https://web.archive.org/web/20230623154505/https://www.cspplaza.com/article-22602-1.html; http://www.cnste.org/html/xiangmu/2023/0619/10868.html; http://www.sh-ihw.com/news/495.html; https://web.archive.org/web/20230627144442/https://www.cspplaza.com/article-22602-1.html; http://web.archive.org/web/20230627151600/http://xj.news.cn/zt/2023-06/19/c_1129706090.htm
CTGR Qinghai Golmud 100 MW Tower + 1000 MW PV | 三峡能源青海格尔木1100MW光伏光热项目100MW光热 | 153 | China | Asia | Under Construction | 100 |  |  |  | PV-Hybrid; Tower | 1000 | 10 | Co-located with 1000 MW PV | 2023 | 2024 | Qinghai | Haixi | Golmud, Wutumeiren | 36.83, 93.27 | [16 empty] | China Three Gorges Renewables (CTGR) | China | [7 empty] | Molten Salt | Salt | [29 empty] | 747500 | 1.2458 | 6460 | 115.75 | [11 empty] | https://www.gem.wiki/Qinghai_Golmud_(Three_Gorges)_1100_MW_solar_power_plant; https://web.archive.org/web/20230629085409/https://en.cspplaza.com/officially-commenced-construction%21-the-100mw-solar-thermal-project-of-golmud-of-three-gorges-energy-contracted-by-china-energy-engineering-group-northwest-china-electric-power-test-research-institute-co.,-ltd-has-started
CSP3 BILANCIA Sicily MS-LFR |  | 154 | Italy | Europe | Under Construction | 4 | [9 empty] | Sicily | Palermo | Mezzojuso | 37.84, 13.52 | [13 empty] | Italian CSP FIT | [11 empty] | Molten Salt | Salt | [10 empty] | 16 | Molten Salt | [9 empty] | Frenell | Italy | [6 empty] | 84000 | [14 empty] | https://www.fatagroup.it/concentrated-solar-power-plant-bilancia-pv-s-r-l-mezzojuso-palermo/
CTGR Quinhai Quingyu DC 100 MW Tower+ 900 MW PV |  |  | China | Asia | Under Construction |  |  |  |  | PV-Hybrid; Tower |  |  |  | 2023 | 2024 | Qinghai | Haixi | Golmud, Wutumeiren | 36.79, 93.36 | [16 empty] | China Three Gorges Renewables (CTGR) | China |  |  |  | Northwest Engineering Corporation(Power China); Cosin Solar; Zhejiang Thermal Power Construction of CEEC | China | [48 empty] | http://en.cnste.org/html/csp/2022/0805/1281.html; https://web.archive.org/web/20230627152440/http://www.cosinsolar.com/upload/file/2023-06/1686055421871457.pdf

## About
CSP.guru 2023-07-01
About: | https://csp.guru/about/
Copyright©: Richard Thonig and Johan Lilliestam, Research Insitute for Sustainability Helmholtz Centre Potsdam,
License: | CC-BY 4.0 | https://creativecommons.org/licenses/by/4.0/legalcode
Suggested citation: |  | Richard Thonig, Alina Glimanova & Johan Lilliestam. (2023). CSP.guru 2023-07-01. https://doi.org/10.5281/zenodo.1318151
Funding: | SolarPACES
Contact: | richard.thonig@rifs-potsdam.de
Archive: | https://doi.org/10.5281/zenodo.1318151